## 1500-IN-LST-0000-EXP-5001_C
Instrument Index
Area Name | Unit Number | Unit Name | Loop Name | Tag Status | Tag Name | Instrument Type | P&ID | Service | Line Number | Equipment | Supply Resp. | I/O SYS | IO Type | I/O Location | Signal Type | Instrument Location | WBS | Power Requirement (Y/N) | JB Preassign | HT Rqd
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4002 | NEW | 1500-FS-4002 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | TG BLDG (NEAR WT CHEM DOSING) | 1-1/2"-TMW-1560-8426-SBJ-FP-ET | 1560-ES-003 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1560-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4002 | NEW | 1500-FAH-4002 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | TG BLDG (NEAR WT CHEM DOSING) | ------ | 1560-ES-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4004 | NEW | 1500-FS-4004 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | TG BLDG (AUX BOILER CHEM DOSING) | 1-1/2"-TMW-1560-8425-SBJ-FP-ET | 1560-ES-002 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1560-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4004 | NEW | 1500-FAH-4004 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | TG BLDG (AUX BOILER CHEM DOSING) | ------ | 1560-ES-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4006 | NEW | 1500-FS-4006 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | ACC DEAERATOR (GRADE) | 1-1/2"-TMW-1560-8424-SBJ-FP-ET | 1560-ES-001 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1560-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4006 | NEW | 1500-FAH-4006 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | ACC DEAERATOR (GRADE) | ------ | 1560-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4008 | NEW | 1500-FS-4008 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | CONV/SH/ECON AREA (GRADE) | 1-1/2"-TMW-1540-8465-SBJ-FP-ET | 1540-ES-004 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4008 | NEW | 1500-FAH-4008 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | CONV/SH/ECON AREA (GRADE) | ------ | 1540-ES-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4010 | NEW | 1500-FS-4010 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | MAIN COMP AREA (GRADE) | 1-1/2"-TMW-1540-8466-SBJ-FP-ET | 1540-ES-003 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4010 | NEW | 1500-FAH-4010 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | MAIN COMP AREA (GRADE) | ------ | 1540-ES-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4012 | NEW | 1500-FS-4012 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | SULFUR BURNER (GRADE) | 1-1/2"-TMW-1540-8419-SBJ-FP-ET | 1540-ES-002 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4012 | NEW | 1500-FAH-4012 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | SULFUR BURNER (GRADE) | ------ | 1540-ES-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4014 | NEW | 1500-FS-4014 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | DEAERATOR (GRADE) | 1-1/2"-TMW-1540-8418-SBJ-FP-ET | 1540-ES-001 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4014 | NEW | 1500-FAH-4014 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | DEAERATOR (GRADE) | ------ | 1540-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4016 | NEW | 1500-FS-4016 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | COOL TWR (CHEM DOSING) | 1-1/2"-TMW-1550-8422-SBJ-FP-ET | 1550-ES-001 | Vendor | DCS | DI | DCS | 24V | FLD-INLINE | 1500 | N | 1550-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4016 | NEW | 1500-FAH-4016 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | COOL TWR (CHEM DOSING) | ------ | 1550-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4026 | NEW | 1500-FS-4026 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | BETWEEN PRODUCT ACID TANKS | 1-1/2"-TMW-1570-8427-SBJ-FP-ET | 1570-ES-004 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1570-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4026 | NEW | 1500-FAH-4026 | DCS Alarm | 1500-PR-PID-0000-EXP-5140 | BETWEEN PRODUCT ACID TANKS | ------ | 1570-ES-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4028 | NEW | 1500-FS-4028 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | START-UP ACID TANK | 1-1/2"-TMW-1570-8428-SBJ-FP-ET | 1570-ES-003 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1570-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4028 | NEW | 1500-FAH-4028 | DCS Alarm | 1500-PR-PID-0000-EXP-5140 | START-UP ACID TANK | ------ | 1570-ES-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4030 | NEW | 1500-FS-4030 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | ACID LOADING (@PLATFORM) | 1-1/2"-TMW-1570-8429-SBJ-FP-ET | 1570-ES-002 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1570-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4030 | NEW | 1500-FAH-4030 | DCS Alarm | 1500-PR-PID-0000-EXP-5140 | ACID LOADING (@PLATFORM) | ------ | 1570-ES-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4032 | NEW | 1500-FS-4032 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5140 | ACID LOADING (@ GRADE) | 1-1/2"-TMW-1570-8430-SBJ-FP-ET | 1570-ES-001 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1570-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4032 | NEW | 1500-FAH-4032 | DCS Alarm | 1500-PR-PID-0000-EXP-5140 | ACID LOADING (@ GRADE) | ------ | 1570-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4040 | NEW | 1500-FAH-4040 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1570 AREA | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4040 | NEW | 1500-XA-4040A | ALARM BEACON | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1570 AREA | -RS--BC-TV-- | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1570-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4040 | NEW | 1500-XA-4040B | ALARM HORN | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1570 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1570-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4042 | NEW | 1500-FAH-4042 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1540 AREA | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4042 | NEW | 1500-XA-4042A | ALARM BEACON | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1540 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4042 | NEW | 1500-XA-4042B | ALARM HORN | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1540 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4044 | NEW | 1500-FAH-4044 | DCS ALARM | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1560 AREA | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4044 | NEW | 1500-XA-4044A | ALARM BEACON | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1560 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1560-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4044 | NEW | 1500-XA-4044B | ALARM HORN | 1500-PR-PID-0000-EXP-5140 | SAFETY SHOWER ACTIVATION 1560 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1560-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4200 | NEW | 1500-FS-4200 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | EFFLUENT NEUTRALIZATION | 1-1/2"-TMW-1520-8434-SBJ-FP-ET | 1520-ES-001 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4200 | NEW | 1500-FAH-4200 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | EFFLUENT NEUTRALIZATION | ------ | 1520-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4202 | NEW | 1500-FS-4202 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | COMB. PMP TK (@ PLATFORM) | 1-1/2"-TMW-1520-8435-SBJ-FP-ET | 1520-ES-002 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4202 | NEW | 1500-FAH-4202 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | COMB. PMP TK (@ PLATFORM) | ------ | 1520-ES-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4204 | NEW | 1500-FS-4204 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | ACID COOLERS (@ GRADE) | 1-1/2"-TMW-1520-8436-SBJ-FP-ET | 1520-ES-003 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4204 | NEW | 1500-FAH-4204 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | ACID COOLERS (@ GRADE) | ------ | 1520-ES-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4206 | NEW | 1500-FS-4206 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | DT (@ GRADE) | 1-1/2"-TMW-1520-8438-SBJ-FP-ET | 1520-ES-004 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4206 | NEW | 1500-FAH-4206 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | DT (@ GRADE) | ------ | 1520-ES-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4208 | NEW | 1500-FS-4208 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | FAT (@ TUBESHEET) | 1-1/2"-TMW-1520-8439-SBJ-FP-ET | 1520-ES-005 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4208 | NEW | 1500-FAH-4208 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | FAT (@ TUBESHEET) | ------ | 1520-ES-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4210 | NEW | 1500-FS-4210 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | DT (@ TUBESHEET) | 1-1/2"-TMW-1520-8440-SBJ-FP-ET | 1520-ES-006 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1540-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4210 | NEW | 1500-FAH-4210 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | DT (@ TUBESHEET) | ------ | 1520-ES-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4212 | NEW | 1500-FS-4212 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | FAT (@ PLATFORM) | 1-1/2"-TMW-1520-8441-SBJ-FP-ET | 1520-ES-007 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4212 | NEW | 1500-FAH-4212 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | FAT (@ PLATFORM) | ------ | 1520-ES-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4214 | NEW | 1500-FS-4214 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | FAT (@ PLATFORM) | 1-1/2"-TMW-1520-8442-SBJ-FP-ET | 1520-ES-008 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4214 | NEW | 1500-FAH-4214 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | FAT (@ PLATFORM) | ------ | 1520-ES-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4216 | NEW | 1500-FS-4216 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | IPAT (@ GRADE) | 1-1/2"-TMW-1520-8448-SBJ-FP-ET | 1520-ES-009 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4216 | NEW | 1500-FAH-4216 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | IPAT (@ GRADE) | ------ | 1520-ES-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4220 | NEW | 1500-FS-4220 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | IPAT (@ 2ND STAGE DISTRIBUTOR) | 1-1/2"-TMW-1520-8450-SBJ-FP-ET | 1520-ES-011 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4220 | NEW | 1500-FAH-4220 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | IPAT (@ 2ND STAGE DISTRIBUTOR) | ------ | 1520-ES-011 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4224 | NEW | 1500-FS-4224 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | IPAT (@ TUBESHEET) | 1-1/2"-TMW-1520-8452-SBJ-FP-ET | 1520-ES-013 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4224 | NEW | 1500-FAH-4224 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | IPAT (@ TUBESHEET) | ------ | 1520-ES-013 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4230 | NEW | 1500-FS-4230 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | PUMP TK SA COOLER AREA | 1-1/2"-TMW-1520-8459-SBJ-FP-ET | 1520-ES-015 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4230 | NEW | 1500-FAH-4230 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | PUMP TK SA COOLER AREA | ------ | 1520-ES-015 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4232 | NEW | 1500-FS-4232 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | INSIDE LAB | 1-1/2"-TMW-1520-8462-SBJ-FP-ET | 1520-ES-016 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-002 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4232 | NEW | 1500-FAH-4232 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | INSIDE LAB | ------ | 1520-ES-016 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4234 | NEW | 1500-FS-4234 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | TAIL GAS SCRUBBER (@ GRADE) | 1-1/2"-TMW-1530-8461-SBJ-FP-ET | 1530-ES-001 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4234 | NEW | 1500-FAH-4234 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | TAIL GAS SCRUBBER (@ GRADE) | ------ | 1530-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4217 | NEW | 1500-FS-4217 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | DT AT PLATFORM | 1-1/2"-TMW-1520-8451-SBJ-FP-ET | 1520-ES-012 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4217 | NEW | 1500-FAH-4217 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | DT AT PLATFORM | ------ | 1520-ES-012 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4215 | NEW | 1500-FS-4215 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | IPAT 2ND STAGE | 1-1/2"-TMW-1520-8449-SBJ-FP-ET | 1520-ES-010 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4215 | NEW | 1500-FAH-4215 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | IPAT 2ND STAGE | ------ | 1520-ES-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4238 | NEW | 1500-FS-4238 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | SVS (@ PUMPS) | 1-1/2"-TMW-1510-8416-SBJ-FP-ET | 1510-ES-004 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4238 | NEW | 1500-FAH-4238 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | SVS (@ PUMPS) | ------ | 1510-ES-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4237 | NEW | 1500-FS-4237 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | SULFUR UNLOADING (NEAR TRUCKS) | 1-1/2"-TMW-1510-8415-SBJ-FP-ET | 1510-ES-003 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4237 | NEW | 1500-FAH-4237 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | SULFUR UNLOADING (NEAR TRUCKS) | ------ | 1510-ES-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4236 | NEW | 1500-FS-4236 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | CAUSTIC STOR (AT TRUCK) | 1-1/2"-TMW-1510-8414-SBJ-FP-ET | 1510-ES-002 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4236 | NEW | 1500-FAH-4236 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | CAUSTIC STOR (AT TRUCK) | ------ | 1510-ES-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4235 | NEW | 1500-FS-4235 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | CAUSTIC STOR (AT PUMPS) | 1-1/2"-TMW-1510-8413-SBJ-FP-ET | 1510-ES-001 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4235 | NEW | 1500-FAH-4235 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | CAUSTIC STOR (AT PUMPS) | ------ | 1510-ES-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4222 | NEW | 1500-FS-4222 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | BETWEEN ACID COOLERS | 1-1/2"-TMW-1520-482-SBJ-FP-ET | 1520-ES-017 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4222 | NEW | 1500-FAH-4222 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | BETWEEN ACID COOLERS | ------ | 1520-ES-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4223 | NEW | 1500-FS-4223 | VENDOR SUPPLY FLOW SWITCH (SAFETY SHOWER) | 1500-PR-PID-0000-EXP-5142 | COMBINATION PUMP TANK (ON PLATFORM) | 1-1/2"-TMW-1500-484-SBJ-FP-ET | 1520-ES-018 | Vendor | DCS | DI | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4223 | NEW | 1500-FAH-4223 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | COMBINATION PUMP TANK (ON PLATFORM) | ------ | 1520-ES-018 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4240 | NEW | 1500-FAH-4240 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1520 AREA | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4240 | NEW | 1500-XA-4240A | ALARM BEACON | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1520 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4240 | NEW | 1500-XA-4240B | ALARM HORN | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1520 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1520-JBP-003 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4242 | NEW | 1500-FAH-4242 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1530 AREA | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4242 | NEW | 1500-XA-4242A | ALARM BEACON | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1530 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4242 | NEW | 1500-XA-4242B | ALARM HORN | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1530 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1530-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-4244 | NEW | 1500-FAH-4244 | DCS ALARM | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1510 AREA | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4244 | NEW | 1500-XA-4244A | ALARM BEACON | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1510 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1510-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-X-4244 | NEW | 1500-XA-4244B | ALARM HORN | 1500-PR-PID-0000-EXP-5142 | SAFETY SHOWER ACTIVATION 1510 AREA | ------ | N/A | Vendor | DCS | DO | RIO | 24V | FLD-INLINE | 1500 | N | 1510-JBP-001 | YES
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9802 | NEW | 1500-FE-9802 | FLOW ELEMENT - ORIFICE PLATE | 1500-PR-PID-0000-EXP-5198 | PROPANE TO STARTUP BURNER | 4"-PRP-1540-0250-CBL-HC- | 1540-PK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9802 | NEW | 1500-FIT-9802 | FLOW TRANSMITTER - D/P | 1500-PR-PID-0000-EXP-5198 | PROPANE TO STARTUP BURNER | ------ | 1540-PK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1500 | N | 1540-JBP-002 | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9802 | NEW | 1500-FI-9802 | DCS INDICATION | 1500-PR-PID-0000-EXP-5198 | PROPANE TO STARTUP BURNER | ------ | 1540-PK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9802 | NEW | 1500-FQI-9802 | DCS TOTALIZATION | 1500-PR-PID-0000-EXP-5198 | PROPANE TO STARTUP BURNER | ------ | 1540-PK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9805 | NEW | 1500-FE-9805 | FLOW ELEMENT - ORIFICE PLATE | 1500-PR-PID-0000-EXP-5198 | PROPANE TO IP AUX BOILER | 4"-PRP-1560-0249-CBL-HC- | 1560-BO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9805 | NEW | 1500-FIT-9805 | FLOW TRANSMITTER - D/P | 1500-PR-PID-0000-EXP-5198 | PROPANE TO IP AUX BOILER | ------ | 1560-BO-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1500 | N | 1540-JBP-002 | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9805 | NEW | 1500-FI-9805 | DCS INDICATION | 1500-PR-PID-0000-EXP-5198 | PROPANE TO IP AUX BOILER | ------ | 1560-BO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-F-9805 | NEW | 1500-FQI-9805 | DCS TOTALIZATION | 1500-PR-PID-0000-EXP-5198 | PROPANE TO IP AUX BOILER | ------ | 1560-BO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-P-9801 | NEW | 1500-PI-9801 | PRESSURE GAUGE | 1500-PR-PID-0000-EXP-5198 | PROPANE TO STARTUP BURNER | 4"-PRP-1540-0250-CBL-HC- | 1540-PK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1500 | N | N/A | NO
1500 | 1500 | SULFURIC ACID PLANT | 1500-P-9804 | NEW | 1500-PI-9804 | PRESSURE GAUGE | 1500-PR-PID-0000-EXP-5198 | PROPANE TO IP AUX BOILER | 4"-PRP-1560-0249-CBL-HC- | 1560-BO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1500 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1003 | NEW | 1510-HS-1003A | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5010 | 1510-PP-001 SULFUR UNLOADING PUMP | ------ | 1510-PP-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1003 | NEW | 1510-HS-1003B | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5010 | 1510-PP-002 SULFUR UNLOADING PUMP | ------ | 1510-PP-002 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1004 | NEW | 1510-HS-1004A | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5010 | 1510-PP-004 SULFUR UNLOADING PUMP | ------ | 1510-PP-004 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1004 | NEW | 1510-HS-1004B | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5010 | 1510-PP-005 SULFUR UNLOADING PUMP | ------ | 1510-PP-005 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1021 | NEW | 1510-AE-1021 | SO2 AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | 6"-ACV-1510-2386-CBT-FP-ST | 1510-ZC-001 | EXP | NA | E-T | NA | mV | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-A-1021 | NEW | 1510-AIT-1021 | SO2 AREA MONITOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1021 | NEW | 1510-AI-1021 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1021 | NEW | 1510-AAH-1021 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1020 | NEW | 1510-TW-1020 | THERMOWELL | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | 6"-ACV-1510-2386-CBT-FP-ST | 1510-ZC-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1020 | NEW | 1510-TE-1020 | TEMPERATURE ELEMENT - TC TYPE K | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | 6"-ACV-1510-2386-CBT-FP-ST | 1510-ZC-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1020 | NEW | 1510-TIT-1020 | TEMPERATURE INDICATING TRANSMITTER | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1020 | NEW | 1510-TI-1020 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1020 | NEW | 1510-TAH-1020 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR PIT VENT TO VAPOR SCRUBBER | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1008 | NEW | 1510-TW-1008 | THERMOWELL | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | N/A | N/A | N/A | mV | FLD-EQUIP | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1008 | NEW | 1510-TE-1008 | TEMPERATURE ELEMENT - TC TYPE K | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1008 | NEW | 1510-TIT-1008 | TEMPERATURE INDICATING TRANSMITTER | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1008 | NEW | 1510-TI-1008 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1008 | NEW | 1510-TAH-1008 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1008 | NEW | 1510-TAL-1008 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LIT-1007A | LEVEL TRANSMITTER - RADAR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-FI-1007A | FLOW GAUGE - ROTAMETER | 1510-PR-PID-0000-EXP-5010 | PURGE FOR LIT-1007A | ------ | 1510-ZC-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LI-1007A | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LAL-1007A | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LALL-1007A | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LAHH-1007A | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSLL-1007A | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSL-1007A | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSH-1007A | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSHH-1007A | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LIT-1007B | BUBBLER LEVEL TRANSMITTER | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-FI-1007B | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LI-1007B | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LAL-1007B | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LALL-1007B | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LAHH-1007B | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSLL-1007B | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSL-1007B | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSH-1007B | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LSHH-1007B | INTLK | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-HS-1007 | DCS SELECTOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LIC-1007 | DCS INDICATION AND CONTROL | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LY-1007 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1007 | NEW | 1510-LCV-1007 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | 6"-MOS-1510-1115-CBT-HC-ST | 1510-ZC-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-Z-1007 | NEW | 1510-ZSC-1007 | PART OF VALVE LIMIT SWITCH | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-Z-1007 | NEW | 1510-ZAC-1007 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1019 | NEW | 1510-AE-1019 | H2S AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1019 | NEW | 1510-AIT-1019 | H2S AREA MONITOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1019 | NEW | 1510-AI-1019 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1019 | NEW | 1510-AAH-1019 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1019 | NEW | 1510-AAHH-1019 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1019 | NEW | 1510-ASH-1019 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1012 | NEW | 1510-AE-1012 | H2S AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1012 | NEW | 1510-AIT-1012 | H2S AREA MONITOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1012 | NEW | 1510-AI-1012 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1012 | NEW | 1510-AAH-1012 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1012 | NEW | 1510-AAHH-1012 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1012 | NEW | 1510-ASH-1012 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1011 | NEW | 1510-XA-1011A | ALARM BEACON | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1011 | NEW | 1510-XA-1011B | ALARM HORN | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1012 | NEW | 1510-XA-1012A | ALARM BEACON | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1012 | NEW | 1510-XA-1012B | ALARM HORN | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1013 | NEW | 1510-PDIT-1013 | PRESSURE TRANSMITTER-D/P SEAL | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | SPY-090 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1013 | NEW | 1510-PDI-1013 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | SPY-090 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1013 | NEW | 1510-PDAH-1013 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | SPY-090 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-AE-1042 | H2S AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-AIT-1042 | H2S AREA MONITOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-AI-1042 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-AAH-1042 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-AAHH-1042 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-ASHH-1042 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT |  | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1042 | NEW | 1510-ASH-1042 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1043 | NEW | 1510-AE-1043 | SO2 AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1043 | NEW | 1510-AIT-1043 | SO2 AREA MONITOR | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1043 | NEW | 1510-AI-1043 | DCS INDICATION | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1043 | NEW | 1510-AAH-1043 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1043 | NEW | 1510-AAHH-1043 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1043 | NEW | 1510-ASH-1043 | DCS ALARM | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1042 | NEW | 1510-XA-1042A | ALARM BEACON | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1042 | NEW | 1510-XA-1042B | ALARM HORN | 1510-PR-PID-0000-EXP-5010 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1100 | NEW | 1510-XC-1100 | GROUND SWITCH | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | 1510-ZC-001 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1510 | 120 VAC/60Hz | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1100 | NEW | 1510-XI-1100 | DCS INDICATION | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1101 | NEW | 1510-XC-1101 | GROUND SWITCH | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | 1510-ZC-001 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1510 | 120 VAC/60Hz | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1101 | NEW | 1510-XI-1101 | DCS INDICATION | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | 1510-ZC-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1118A | NEW | 1510-XA-1118A | ALARM BEACON | 1510-PR-PID-0000-EXP-5011 | SULFUR TRUCK UNLOADING STATION | ------ | 1510-ZC-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-AE-1141 | H2S AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-AIT-1141 | H2S AREA MONITOR | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-AI-1141 | DCS INDICATION | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-AAH-1141 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-AAHH-1141 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-ASHH-1141 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1141 | NEW | 1510-ASH-1141 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-AE-1142 | H2S AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-AIT-1142 | H2S AREA MONITOR | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-AI-1142 | DCS INDICATION | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-AAH-1142 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-AAHH-1142 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-ASHH-1142 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1142 | NEW | 1510-ASH-1142 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-AE-1143 | SO2 AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5011 | SLFUR UNLOADING BAYS | ------ | N/A | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-AIT-1143 | SO2 AREA MONITOR | 1510-PR-PID-0000-EXP-5011 | SLFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-AI-1143 | DCS INDICATION | 1510-PR-PID-0000-EXP-5011 | SLFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-AAH-1143 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SLFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-AAHH-1143 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-ASH-1143 | DCS ALARM | 1510-PR-PID-0000-EXP-5011 | SLFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1143 | NEW | 1510-ASHH-1143 | INTLK | 1510-PR-PID-0000-EXP-5011 | 1510-ZC-001 SULFUR UNLOADING PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1141A | NEW | 1510-XA-1141A | ALARM BEACON | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1141B | NEW | 1510-XA-1141B | ALARM HORN | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1142A | NEW | 1510-XA-1142A | ALARM BEACON | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1142B | NEW | 1510-XA-1142B | ALARM HORN | 1510-PR-PID-0000-EXP-5011 | SULFUR UNLOADING BAYS | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1201 | NEW | 1510-LIT-1201 | LEVEL TRANSMITTER - RADAR | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1201 | NEW | 1510-LI-1201 | DCS INDICATION | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1201 | NEW | 1510-LAL-1201 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1201 | NEW | 1510-LAH-1201 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1201 | NEW | 1510-LSHH-1201 | INTLK | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1202 | NEW | 1510-LIT-1202 | BUBBLER LEVEL TRANSMITTER | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1202 | NEW | 1510-LI-1202 | DCS INDICATION | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1202 | NEW | 1510-LSHH-1202 | INTLK | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1202 | NEW | 1510-FI-1202 | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1510-PR-PID-0000-EXP-5012 | 1510-LIT-1202 PURGE | ------ | 1510-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1202 | NEW | 1510-LAL-1202 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1202 | NEW | 1510-LAH-1202 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1205 | NEW | 1510-TW-1205 | THERMOWELL | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | 6"-ACV-1510-1201-CBT-FP-ST | 1510-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1205 | NEW | 1510-TE-1205 | TEMPERATURE ELEMENT - TC TYPE K | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | 6"-ACV-1510-1201-CBT-FP-ST | 1510-TK-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1205 | NEW | 1510-TIT-1205 | TEMPERATURE INDICATING TRANSMITTER | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1205 | NEW | 1510-TI-1205 | DCS INDICATION | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1205 | NEW | 1510-TAH-1205 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1206 | NEW | 1510-AE-1206 | SO2 AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | 6"-ACV-1510-1201-CBT-FP-ST | 1510-TK-001 | EXP | NA | E-T | NA | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1206 | NEW | 1510-AIT-1206 | SO2 AREA MONITOR | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1206 | NEW | 1510-AI-1206 | DCS INDICATION | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK |  | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1206 | NEW | 1510-AAH-1206 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-AE-1242 | SO2 AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-AIT-1242 | SO2 AREA MONITOR | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-AI-1242 | DCS INDICATION | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-AAH-1242 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-ASH-1242 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-AAHH-1242 | DCS ALARM | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1242 | NEW | 1510-ASHH-1242 | INTLK | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1242A | NEW | 1510-XA-1242A | ALARM BEACON | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1242B | NEW | 1510-XA-1242B | ALARM HORN | 1510-PR-PID-0000-EXP-5012 | 1510-TK-001 LIQUID SULFUR STOR TK | ------ | 1510-TK-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1502 | NEW | 1510-AE-1502 | SO2 AREA MONITOR SENSOR | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | 10"-ACV-1510-2387-CBT-FP-ST | 1510-SR-001 | EXP | NA | E-T | NA | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1502 | NEW | 1510-AIT-1502 | SO2 AREA MONITOR | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1502 | NEW | 1510-AI-1502 | DCS INDICATION | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1502 | NEW | 1510-AAH-1502 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1501 | NEW | 1510-TW-1501 | THERMOWELL | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | 10"-ACV-1510-2387-CBT-FP-ST | 1510-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1501 | NEW | 1510-TE-1501 | TEMPERATURE ELEMENT - TC TYPE K | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | 10"-ACV-1510-2387-CBT-FP-ST | 1510-SR-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1501 | NEW | 1510-TIT-1501 | TEMPERATURE INDICATING TRANSMITTER | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1501 | NEW | 1510-TI-1501 | DCS INDICATION | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1501 | NEW | 1510-TAH-1501 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TW-1504 | VENDOR SUPPLY THERMOWELL | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TE-1504 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TIT-1504 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | Vendor | PLC | AI-HART-S | DCS | 4-20mA HART | PECS | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TI-1504 | DCS INDICATION | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TAH-1504 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TAHH-1504 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-1504 | NEW | 1510-TAL-1504 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-SR-001 SVS ACIDIC VENT INLET | ------ | 1510-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LIC-1524 | VENDOR INTERFACE | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | PLC | AI-HART-S | DCS | 4-20mA HART | PECS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LY-1524 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LCV-1524 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | 1"-PCD-1510-0106-SBA-FP-ET | 1510-PK-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LAL-1524 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LAH-1524 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LALL-1524 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LAHH-1524 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LSLL-1524 | INTLK | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-1524 | NEW | 1510-LSHH-1524 | INTLK | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1512 | NEW | 1510-HIC-1512 | DCS OPERATOR INITIATED CONTROL | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1512 | NEW | 1510-HS-1512 | DCS OPERATOR INITIATED CONTROL | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1512 | NEW | 1510-XEV-1512 | SOLENOID VALVE | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | 1"-PCD-1510-1515-SBA-FP-ET | 1510-PK-007 | EXP | DCS | DO | RIO | 24V | FLD-INLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1512 | NEW | 1510-HV-1512 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | 1"-PCD-1510-1515-SBA-FP-ET | 1510-PK-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-X-1524 | NEW | 1510-XI-1524 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1119A | NEW | 1510-XA-1119A | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | PLC | DI-S | DCS | 24V | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1512 | NEW | 1510-XI-1512 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1512 | NEW | 1510-HY-1512 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | ------ | 1510-PK-007 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-1526 | NEW | 1510-HS-1526 | DCS OPERATOR INITIATED CONTROL | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS |  | 1510-PK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-1526 | NEW | 1510-XEV-1526 | SOLENOID VALVE | 1510-PR-PID-0000-EXP-5015 | 1510-PK-007 SVS | 1"-PCD-1510-1515-SBA-FP-ET | 1510-PK-007 | EXP | DCS | DO | RIO | 24V | FLD-INLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1523 | NEW | 1510-AE-1523 | ORP ELEMENT | 1510-PR-PID-0000-EXP-5015 | 1510-PK-014 HYDROGEN PEROXIDE DOSING | 1"-ACW-1510-1516-SBO-FP-ET | 1510-PK-014 | EXP | NA | E-T | NA | mV | DCS | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-A-1523 | NEW | 1510-AIT-1523 | ORP TRANSMITTER | 1510-PR-PID-0000-EXP-5015 | 1510-PK-014 HYDROGEN PEROXIDE DOSING | ------ | 1510-PK-014 | EXP | DCS | AI-HART | RIO | 4-20mA HART | DCS | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1523 | NEW | 1510-AIC-1523 | DCS CONTROL FUNCTION | 1510-PR-PID-0000-EXP-5015 | 1510-PK-014 HYDROGEN PEROXIDE DOSING | ------ | 1510-PK-014 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1523 | NEW | 1510-AAH-1523 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-014 HYDROGEN PEROXIDE DOSING |  | 1510-PK-014 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-1523 | NEW | 1510-AAL-1523 | DCS ALARM | 1510-PR-PID-0000-EXP-5015 | 1510-PK-014 HYDROGEN PEROXIDE DOSING |  | 1510-PK-014 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1804 | NEW | 1510-PI-1804 | PRESSURE GAUGE | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 4"-LPS-1510-1134-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1811 | NEW | 1510-PIT-1811 | PRESSURE TRANSMITTER | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 4"-LPS-1510-1134-CBO-HC- | N/A | EXP | AI-HART | DCS | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1811 | NEW | 1510-PIC-1811 | DCS INDICATION AND CONTROL | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1811 | NEW | 1510-PAL-1811 | DCS ALARM | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1811 | NEW | 1510-PAH-1811 | DCS ALARM | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1811 | NEW | 1510-PY-1811 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1811 | NEW | 1510-PCV-1811 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 4"-LPS-1510-1134-CBO-HC- | N/A | EXP | NA | NA | NA | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1816 | NEW | 1510-PSV-1816 | PRESSURE RELIEF VALVE | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 4"-LPS-1510-1134-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1805 | NEW | 1510-PI-1805 | PRESSURE GAUGE | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 1"-LPS-1510-1137-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1813 | NEW | 1510-PIT-1813 | PRESSURE TRANSMITTER | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 1"-LPS-1510-1137-CBO-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1813 | NEW | 1510-PIC-1813 | DCS INDICATION AND CONTROL | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1813 | NEW | 1510-PAL-1813 | DCS ALARM | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1813 | NEW | 1510-PAH-1813 | DCS ALARM | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1813 | NEW | 1510-PY-1813 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1813 | NEW | 1510-PCV-1813 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 1"-LPS-1510-1137-CBO-HC- | N/A | EXP | NA | NA | NA | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-1817 | NEW | 1510-PSV-1817 | PRESSURE RELIEF VALVE | 1510-PR-PID-0000-EXP-5018 | SULFUR AREA STEAM DISTRIBUTION | 1"-LPS-1510-1137-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2402 | NEW | 1510-AE-2402 | ANALYZER SENSOR - CONDUCTIVITY | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | 2"-LCD-1510-1185-CBO-HC- | 1510-PK-002 | EXP | NA | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2402 | NEW | 1510-AIT-2402 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | ------ | 1510-PK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2402 | NEW | 1510-AI-2402 | DCS INDICATION | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | ------ | 1510-PK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2402 | NEW | 1510-AAH-2402 | DCS ALARM | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | ------ | 1510-PK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2403 | NEW | 1510-AE-2403 | ANALYZER SENSOR - CONDUCTIVITY | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | 3"-LCD-1510-8619-CBO-HC-ET | 1510-PK-003 | EXP | NA | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-A-2403 | NEW | 1510-AIT-2403 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | ------ | 1510-PK-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2403 | NEW | 1510-AI-2403 | DCS INDICATION | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | ------ | 1510-PK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-A-2403 | NEW | 1510-AAH-2403 | DCS ALARM | 1510-PR-PID-0000-EXP-5024 | SA1 COND. COLLECTION HEADER | ------ | 1510-PK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-2412 | NEW | 1510-XA-2412 | VENDOR INTERFACE | 1510-PR-PID-0000-EXP-5024 | SULFUR AREA COND. COLLECTION SYS | ------ | 1510-PK-002 | Vendor | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-2413 | NEW | 1510-XA-2413 | VENDOR INTERFACE | 1510-PR-PID-0000-EXP-5024 | SULUR PIT COILS COND. COLLECTION SYS | ------ | 1510-PK-003 | Vendor | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9510 | NEW | 1510-FE-9510 | FLOW ELEMENT - ORIFICE PLATE | 1510-PR-PID-0000-EXP-5195 | PROCESS COND. TO CAUSTIC DILUTION | 2"-PCD-1560-0251-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9510 | NEW | 1510-FIT-9510 | FLOW TRANSMITTER - D/P | 1510-PR-PID-0000-EXP-5195 | PROCESS COND. TO CAUSTIC DILUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9510 | NEW | 1510-FIC-9510 | DCS INDICATION AND CONTROL | 1510-PR-PID-0000-EXP-5195 | PROCESS COND. TO CAUSTIC DILUTION | ------ | N/A | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9510 | NEW | 1510-FY-9510 | DCS CALCULATION | 1510-PR-PID-0000-EXP-5195 | PROCESS COND. TO CAUSTIC DILUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9510 | NEW | 1510-FY-9510 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5195 | PROCESS COND. TO CAUSTIC DILUTION | ------ | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-F-9510 | NEW | 1510-FCV-9510 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5195 | PROCESS COND. TO CAUSTIC DILUTION | 2"-PCD-1560-0251-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FE-9511 | FLOW ELEMENT - ORIFICE PLATE | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH | 2"-CAS-1510-0258-SBA-FP-ET | 1510-PP-007/008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FIT-9511 | FLOW TRANSMITTER - D/P | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH | ------ | 1510-PP-007/008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FI-9511 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH |  | 1510-PP-007/008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FIC-9511 | DCS INDICATION AND CONTROL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH | ------ | 1510-PP-007/008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FAL-9511 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH | ------ | 1510-PP-007/008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FY-9511 | SMART VALVE POSITIONER | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH | ------ | 1510-PP-007/008 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-F-9511 | NEW | 1510-FCV-9511 | CONTROL VALVE | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP DISCH | 2"-CAS-1510-9502-SBA-FP-ET | 1510-PP-007/008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-T-9513 | NEW | 1510-TW-9513 | THERMOWELL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP SUCTION | 4"-CAS-1510-0252-SBA-FP-ET | 1510-PP-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-9513 | NEW | 1510-TI-9513 | TEMPERATURE GAUGE | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP SUCTION | 4"-CAS-1510-0252-SBA-FP-ET | 1510-PP-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9512A | NEW | 1510-HS-9512A | START/STOP SWITCH | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP | ------ | 1510-PP-003 | EXP | N/A | DO | N/A | 24V | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9512 | NEW | 1510-JI-9512 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP POWER MONITOR | ------ | 1510-PP-003 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9512 | NEW | 1510-IAL-9512 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP LOW AMP SHUTDOWN | ------ | 1510-PP-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9512 | NEW | 1510-HS-9512 | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP | ------ | 1510-PP-003 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9520 | NEW | 1510-HS-9520 | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC FEED PUMP | ------ | 1510-PP-007 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9524 | NEW | 1510-HS-9524 | MOTOR CONTROL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC FEED PUMP | ------ | 1510-PP-008 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1510 | N | SWRK | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-9514 | NEW | 1510-PI-9514 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING PUMP OUTLET | 3"-CAS-1510-0254-SBA-FP-ET | 1510-PP-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-P-9523 | NEW | 1510-PI-9523 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC FEED PUMP OUTLET | 2"-CAS-1510-0258-SBA-FP-ET | 1510-PP-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-P-9526 | NEW | 1510-PI-9526 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC PUMP DISCH | 2"-CAS-1510-0262-SBA-FP-ET | 1510-PP-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-T-9515 | NEW | 1510-TW-9515 | THERMOWELL | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK TEMP | ------ | 1510-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-9515 | NEW | 1510-TE-9515 | TEMPERATURE ELEMENT - TC TYPE K | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK TEMP | ------ | 1510-TK-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-9515 | NEW | 1510-TIT-9515 | TEMPERATURE INDICATING TRANSMITTER | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK TEMP | ------ | 1510-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-9515 | NEW | 1510-TI-9515 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK TEMP | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-9515 | NEW | 1510-TAL-9515 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK TEMP | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-T-9515 | NEW | 1510-TAH-9515 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK TEMP | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-9529 | NEW | 1510-PIT-9529 | PRESSURE TRANSMITTER - DIAPHRAGM SEAL | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | 2"-CAS-1560-9533-CBN-FP-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INLINE | 1510 | N | 1510-JBP-001 | YES
1500 | 1510 | LIQUID SULFUR | 1510-P-9529 | NEW | 1510-PIC-9529 | DCS CONTROL FUNCTION | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-9529 | NEW | 1510-PSL-9529 | INTLK | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-P-9528 | NEW | 1510-PRV-9528 | SELF REGULATING VALVE | 1510-PR-PID-0000-EXP-5195 | CAUSTIC RECYCLE LINE | 1"-CAS-1510-0265-SBA-FP-ET | 1510-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-D-9527 | NEW | 1510-DE-9527 | CORIOLIS FLOW ELEMENT | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | 2"-CAS-1560-9533-CBN-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-D-9527 | NEW | 1510-DIT-9527 | CORIOLIS FLOW TRANSMITTER | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-D-9527 | NEW | 1510-DI-9527 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-D-9527 | NEW | 1510-DAL-9527 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-D-9527 | NEW | 1510-DAH-9527 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | 20% CAUSTIC SOLUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LIT-9516 | LEVEL TRANSMITTER - RADAR | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LI-9516A | PROCESS INDICATOR | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | N/A | N/A | N/A | 24V | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LI-9516B | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LAL-9516 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LAH-9516 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LSLL-9516 | INTLK | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9516 | NEW | 1510-LSHH-9516 | INTLK | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-H-9516 | NEW | 1510-HS-9516 | OPERATOR INITIATED DCS SELECTOR | 1510-PR-PID-0000-EXP-5195 | CAUSTIC TK LEVEL | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9517 | NEW | 1510-LIT-9517 | LEVEL TRANSMITTER - GWR | 1510-PR-PID-0000-EXP-5195 | 1510-TK-002 CAUSTIC TK | ------ | 1510-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9517 | NEW | 1510-LI-9517A | PROCESS INDICATOR | 1510-PR-PID-0000-EXP-5195 | 1510-TK-002 CAUSTIC TK | ------ | 1510-TK-002 | EXP | N/A | N/A | N/A | 24V | FLD-OFFLINE | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9517 | NEW | 1510-LI-9517B | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | 1510-TK-002 CAUSTIC TK | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9517 | NEW | 1510-LAL-9517 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | 1510-TK-002 CAUSTIC TK | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-L-9517 | NEW | 1510-LAH-9517 | DCS ALARM | 1510-PR-PID-0000-EXP-5195 | 1510-TK-002 CAUSTIC TK | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-XEV-9530 | SOLENOID VALVE | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-XV-9530 | ON/OFF VALVE | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | 2"-CAS-1560-9533-CBN-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1510 | N | N/A | YES
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-HS-9530 | DCS CONTROL FUNCTION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-ZSC-9530 | PART OF VALVE LIMIT SWITCH | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | ------ | N/A | EXP | DCS | DI | RIO | 24V | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-ZAC-9530 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-ZSO-9530 | PART OF VALVE LIMIT SWITCH | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | ------ | N/A | EXP | DCS | DI | RIO | 24V | FLD-INT | 1510 | N | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9530 | NEW | 1510-ZAO-9530 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC SOLUTION TO LITHIUM PROCESSING PLANT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-2501 | NEW | 1540-AE-2501 | ANALYZER SENSOR - CONDUCTIVITY | 1540-PR-PID-0000-EXP-5025 | LOW PRESS COND. TO COND. TK | 2"-LCD-1540-1101-CBO-HC- | 1540-PK-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-2501 | NEW | 1540-AIT-2501 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1540-PR-PID-0000-EXP-5025 | LOW PRESS COND. TO COND. TK | ------ | 1540-PK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-A-2501 | NEW | 1540-AI-2501 | DCS INDICATION | 1540-PR-PID-0000-EXP-5025 | LOW PRESSCOND. TO COND. TK | ------ | 1540-PK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-2501 | NEW | 1540-AAH-2501 | DCS ALARM | 1540-PR-PID-0000-EXP-5025 | LOW PRESS COND. TO COND. TK | ------ | 1540-PK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2510 | NEW | 1540-XA-2510 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5025 | SA1 COND. COLLECTION SYS | ------ | 1540-PK-002 | Vendor | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-2600 | NEW | 1540-PIT-2600 | PRESSURE TRANSMITTER - DIAPHRAGM SEAL | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | 4"-MOS-1510-1120-CCT-HC-ST | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | YES
1500 | 1540 | CONTACT SECTION | 1540-P-2600 | NEW | 1540-PI-2600 | DCS INDICATION | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-2602 | NEW | 1540-FE-2602 | CORIOLIS FLOW ELEMENT | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | 4"-MOS-1510-1120-CCT-HC-ST | 1540-ZM-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-F-2602 | NEW | 1540-FIT-2602 | CORIOLIS FLOW TRANSMITTER | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-2602 | NEW | 1540-FIC-2602 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-2602 | NEW | 1540-FY-2602 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-2602 | NEW | 1540-FCV-2602 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | 4"-MOS-1510-1120-CCT-HC-ST | 1540-ZM-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-2604 | NEW | 1540-PIT-2604 | PRESSURE TRANSMITTER - DIAPHRAGM SEAL | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | 4"-MOS-1510-1120-CCT-HC-ST | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | YES
1500 | 1540 | CONTACT SECTION | 1540-P-2604 | NEW | 1540-PAL-2604 | DCS ALARM | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-2604 | NEW | 1540-PAH-2604 | DCS ALARM | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-2604 | NEW | 1540-PI-2604 | DCS INDICATION | 1540-PR-PID-0000-EXP-5026 | LIQUID SULFUR TO SPRAY NOZZLES | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-2800 | NEW | 1540-PI-2800 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 2"-LPS-1510-2384-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TW-2831A | THERMOWELL | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2320-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TI-2831A | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2320-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TW-2831B | THERMOWELL | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2331-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TI-2831B | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2331-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TW-2831C | THERMOWELL | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2332-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TI-2831C | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2332-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TW-2831D | THERMOWELL | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2333-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TI-2831D | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2333-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TW-2831E | THERMOWELL | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2334-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-2831 | NEW | 1540-TI-2831E | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5028 | LP STEAM TO SUFUR SPRAY NOZZLES | 1/2"-LPS-1540-2334-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-2910 | NEW | 1540-PI-2910 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5029 | PROPANE TO STARTUP BURNER | 4"-PRP-1500-0250-CBL-HC- | 1540-PK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-2911 | NEW | 1540-PI-2911 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5029 | INSTRUMENT AIR TO STARTUP BURNER | 3/4"-INA-1540-0161-CBK-- | 1540-PK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2994 | NEW | 1540-XA-2994 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | STARTUP BURNER PANEL LOSS OF PANEL PURGE | ------ | 1540-PK-001 | EXP | PLC | DI-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2990 | NEW | 1540-XI-2990 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | STARTUP BURNER PANEL PURGE FORCE | ------ | 1540-PK-001 | EXP | PLC | DI-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-2995 | NEW | 1540-BALL-2995 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | FLAME FAILURE | ------ | 1540-PK-001 | EXP | PLC | DI-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2995 | NEW | 1540-XI-2995 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | STARTUP BURNER T.O. RUNNING STATUS | ------ | 1540-PK-001 | EXP | PLC | DI-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2991 | NEW | 1540-XI-2991 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | LOW FIRE RELEASE | ------ | 1540-PK-001 | EXP | PLC | DI-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2992 | NEW | 1540-XA-2992 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | STARTUP BURNER COMMON ALARM | ------ | 1540-PK-001 | EXP | PLC | DI-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-2993 | NEW | 1540-XE-2993 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5029 | REMOTE ESD | ------ | 1540-PK-001 | EXP | PLC | DO-S | DCS | 24V | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4070 | NEW | 1540-FE-4070 | FLOW ELEMENT - AVERAGING PITOT TUBE | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | 96"-SOX-1520-2101-316LSS-HC- | 1540-GB-001 | EXP | NA | E-T | N/A | E-T | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4070 | NEW | 1540-FIT-4070 | FLOW TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4070 | NEW | 1540-FI-4070 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4071 | NEW | 1540-TW-4071 | VENDOR SUPPLY THERMOWELL | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION TEMPERATURE | 96"-SOX-1520-2101-316LSS-HC- | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4071 | NEW | 1540-TE-4071 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION TEMPERATURE | 96"-SOX-1520-2101-316LSS-HC- | 1540-GB-001 | Vendor | N/A | E-T | N/A | E-T | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4071 | NEW | 1540-TIT-4071 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION TEMPERATURE | ------ | 1540-GB-001 | Vendor | PLC | AI-HART-S | PLC | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4072 | NEW | 1540-PIT-4072 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | 96"-SOX-1520-2101-316LSS-HC- | 1540-GB-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4072 | NEW | 1540-PI-4072 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-HCV-4030 | VENDOR SUPPLY INLET GUIDE VANE | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | 96"-SOX-1520-2101-316LSS-HC- | 1540-GB-001 | Vendor | NA | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-HY-4030 | VENDOR SUPPLY SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | Vendor | PLC | AO-HART-S | PLC | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-ZSC-4030 | PART OF VALVE LIMIT SWITCH | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | EXP | PLC | DI-S | PLC | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-ZT-4030 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | Vendor | PLC | AI-HART-S | PLC | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-HS-4030 | OPERATOR INITIATED DCS CONTROL | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION START-UP/NORMAL | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | PLC | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-ZI-4030 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4030 | NEW | 1540-HIC-4030 | OPERATOR INITIATED DCS CONTROL | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP SUCTION CAPACITY CONTROL | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | PLC | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4002 | NEW | 1540-PIT-4002 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | 78"-SOX-1540-2102-304SS-HC- | 1540-GB-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4002 | NEW | 1540-PI-4002 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4002 | NEW | 1540-PAL-4002 | DCS ALARM | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4002 | NEW | 1540-PAH-4002 | DCS ALARM | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4002 | NEW | 1540-PSLL-4002 | INTLK | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4010 | NEW | 1540-PI-4010 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | 78"-SOX-1540-2102-304SS-HC- | 1540-GB-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4020 | NEW | 1540-TW-4020 | THERMOWELL | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | 78"-SOX-1540-2102-304SS-HC- | 1540-GB-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4020 | NEW | 1540-TE-4020 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | 78"-SOX-1540-2102-304SS-HC- | 1540-GB-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4020 | NEW | 1540-TIT-4020 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4020 | NEW | 1540-TI-4020 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1096 | NEW | 1540-TAHH-1096 | DCS ALARM | 1540-PR-PID-0000-EXP-5040 | LUBRICATION OIL TEMP HH FOR COMP SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1096 | NEW | 1540-TI-1096 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | LUBRICATION OIL TEMP HH FOR COMP SHUTDOWN | ------ | 1540-GB-001 | EXP | PLC | AI-HART-S | DCS | 4-20mA HART | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1096 | NEW | 1540-PALL-1096 | DCS ALARM | 1540-PR-PID-0000-EXP-5040 | LUBRICATION OIL PRESSURE LL FOR COMP SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1096 | NEW | 1540-PI-1096 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | LUBRICATION OIL PRESS LL FOR COMP SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4080 | NEW | 1540-FI-4080 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INT | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4080 | NEW | 1540-ZT-4080 | POSITION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | N
1500 | 1540 | CONTACT SECTION | 1540-H-4080 | NEW | 1540-ZI-4080 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4080 | NEW | 1540-HS-4080 | OPERATOR INITIATED DCS SELECTOR | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4080 | NEW | 1540-XV-4080 | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH | 78"-SOX-1540-2102-304SS-HC- | 1540-GB-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4081 | NEW | 1540-FV-4081 | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH TO DT | 36"-SOX-1540-2103-304SS-PP- | 1540-GB-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4081 | NEW | 1540-ZT-4081 | POSITION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH TO DT | ------ | 1540-GB-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4081 | NEW | 1540-ZI-4081 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH TO DT | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4081 | NEW | 1540-FI-4081 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5040 | 1540-GB-001 MAIN COMP DISCH TO DT | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INT | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4081 | NEW | 1540-HS-4081 | OPERATOR INITIATED DCS CONTROL | 1540-PR-PID-0000-EXP-5040 | PLANT AIR TO TWIN BLADE PURGE |  | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4200 | NEW | 1540-PDIT-4200 | PRESSURE TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE INLET AND 1540-ZP-009 JUG VALVE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4200 | NEW | 1540-PDI-4200 | DCS INDICATION | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE INLET AND 1540-ZP-009 JUG VALVE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4200 | NEW | 1540-PDSH-4200 | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE INLET AND 1540-ZP-009 JUG VALVE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4200 | NEW | 1540-PDAL-4200 | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE INLET AND 1540-ZP-009 JUG VALVE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4200 | NEW | 1540-PDALL-4200 | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE INLET AND 1540-ZP-009 JUG VALVE OUTLET |  | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4200 | NEW | 1540-PDSLL-4200 | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE INLET AND 1540-ZP-009 JUG VALVE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4201 | NEW | 1540-FI-4201 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5042 | PURGE FOR PDIT-4200 | ------ | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4202 | NEW | 1540-FI-4202 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5042 | PURGE FOR PDIT-4200 | ------ | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TW-4220A | THERMOWELL | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TE-4220A | TEMPERATURE ELEMENT - TC TYPE R | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | E-T | N/A | E-T | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TIT-4220A | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TI-4220A | DCS INDICATION | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAHH-4220A | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAL-4220A | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAH-4220A | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TW-4220B | THERMOWELL | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TE-4220B | TEMPERATURE ELEMENT - TC TYPE R | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | E-T | N/A | E-T | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TIT-4220B | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TI-4220B | DCS INDICATION | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAHH-4220B | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAL-4220B | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAH-4220B | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TW-4220C | THERMOWELL | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TE-4220C | TEMPERATURE ELEMENT - TC TYPE R | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | E-T | N/A | E-T | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TIT-4220C | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TI-4220C | DCS INDICATION | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAHH-4220C | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAH-4220C | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TAL-4220C | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TSHH-4220A | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TSHH-4220B | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TSHH-4220C | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TSHH-4220 | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TSLL-4220 | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TY-4220 | DCS CONTROL FUNCTION | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-TIC-4220 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4220 | NEW | 1540-HS-4220 | DCS SELECTOR | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE OUTLET |  | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4282 | NEW | 1540-HS-4282 | LOCAL START/STOP SWITCH | 1540-PR-PID-0000-EXP-5042 | JUG VALVE REMOTE LOCAL | ------ | 1540-ZP-009 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4282 | NEW | 1540-HS-4282A | LOCAL START/STOP SWITCH | 1540-PR-PID-0000-EXP-5042 | JUG VALVE REMOTE LOCAL STOP | ------ | 1540-ZP-009 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4282 | NEW | 1540-HIC-4282 | DCS OPERATOR INITIATED CONTROL | 1540-PR-PID-0000-EXP-5042 | JUG VALVE CONTROL | ------ | 1540-ZP-009 | EXP | DCS | AO-HART | RIO | 4-20mA HART | DCS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4282 | NEW | 1540-ZT-4282 | POSITION TRANSMITTER | 1540-PR-PID-0000-EXP-5042 | JUG VALVE POSITION | ------ | 1540-ZP-009 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4282 | NEW | 1540-ZI-4282 | DCS INDICATION | 1540-PR-PID-0000-EXP-5042 | JUG VALVE POSITION | ------ | 1540-ZP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4282 | NEW | 1540-FI-4282 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5042 | JUG VALVE PURGE | ------ | 1540-ZP-009 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4281 | NEW | 1540-HCV-4281 | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5042 | 1540-ZP-009 JUG VALVE | 78"-SOX-1540-2106-304SS-HC- | 1540-ZP-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4281 | NEW | 1540-HY-4281 | VENDOR SUPPLY SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5042 | 1540-ZP-009 JUG VALVE |  | 1540-ZP-009 | EXP | DCS | AO-HART | DCS | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4281 | NEW | 1540-HIC-4281 | DCS OPERATOR INITIATED CONTROL | 1540-PR-PID-0000-EXP-5042 | 1540-ZP-009 JUG VALVE | ------ | 1540-ZP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4281 | NEW | 1540-FI-4281 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5042 | 1540-ZP-009 JUG VALVE | ------ | 1540-ZP-009 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7841 | NEW | 1540-AE-7841 | SO2 AREA MONITOR SENSOR | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE | ------ | 1540-ZP-007 | EXP | N/A | E-T | N/A | mV | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7841 | NEW | 1540-AIT-7841 | SO2 AREA MONITOR | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7841 | NEW | 1540-AAI-7841 | DCS INDICATION | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7841 | NEW | 1540-AAH-7841 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | SOFTWARE | RIO | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7841 | NEW | 1540-AAHH-7841 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | SOFTWARE | RIO | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7841 | NEW | 1540-ASH-7841 | INTLK | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | SOFTWARE | RIO | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7241 | NEW | 1540-AE-7241 | SO2 AREA MONITOR | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | N/A | E-T | N/A | mV | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7241 | NEW | 1540-AIT-7241 | SO2 AREA MONITOR | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7241 | NEW | 1540-AAH-7241 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7241 | NEW | 1540-AAHH-7241 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7241 | NEW | 1540-ASH-7241 | INTLK | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4242 | NEW | 1540-AE-4242 | SO2 AREA MONITOR SENSOR | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4242 | NEW | 1540-AIT-4242 | SO2 AREA MONITOR | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4242 | NEW | 1540-AI-4242 | DCS INDICATION | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4242 | NEW | 1540-AAHH-4242 | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4242 | NEW | 1540-AAH-4242 | DCS ALARM | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4242 | NEW | 1540-ASH-4242 | INTLK | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-4242A | NEW | 1540-XA-4242A | ALARM BEACON | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-4242B | NEW | 1540-XA-4242B | ALARM HORN | 1540-PR-PID-0000-EXP-5042 | 1540-ZM-001 SULFUR FURNACE | ------ | 1540-ZM-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4820 | NEW | 1540-TW-4820 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | 78"-SOX-1540-2107-304SS-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4820 | NEW | 1540-TE-4820 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | 78"-SOX-1540-2107-304SS-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4820 | NEW | 1540-TIT-4820 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4820 | NEW | 1540-TI-4820 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4820 | NEW | 1540-TAL-4820 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4820 | NEW | 1540-TAH-4820 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4850 | NEW | 1540-PIT-4850 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | 78"-SOX-1540-2107-304SS-HC- | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4850 | NEW | 1540-PI-4850 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV PGS INLET | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-4852 | NEW | 1540-FI-4852 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5048 | PRESS TRANSMITTER PURGE | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-4830 | NEW | 1540-BV-4830 | MANUAL DAMPER | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV 4TH PASS PREHEAT DUCT | 42"-SOX-1540-2109-304SS-HC- | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-4830 | NEW | 1540-FI-4830 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5048 | 1540-BV-4830 PURGE LINE | ------ | 1540-RE-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-4832 | NEW | 1540-BV-4832 | MANUAL DAMPER | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV 3RD PASS PREHEAT DUCT | 42"-SOX-1540-2117-304SS-HC- | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-4832 | NEW | 1540-FI-4832 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5048 | 1540-BV-4832 PURGE LINE | ------ | 1540-RE-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-4833 | NEW | 1540-BV-4833 | MANUAL DAMPER | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV 2ND PASS PREHEAT DUCT | 42"-SOX-1540-2116-304SS-HC- | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-4833 | NEW | 1540-FI-4833 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5048 | 1540-BV-4833 PURGE LINE | ------ | 1540-RE-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4825 | NEW | 1540-TW-4825 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4825 | NEW | 1540-TE-4825 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4825 | NEW | 1540-TIT-4825 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4825 | NEW | 1540-TI-4825 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4826 | NEW | 1540-TW-4826 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4826 | NEW | 1540-TE-4826 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4826 | NEW | 1540-TIT-4826 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4826 | NEW | 1540-TI-4826 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4827 | NEW | 1540-TW-4827 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4827 | NEW | 1540-TE-4827 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4827 | NEW | 1540-TIT-4827 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4827 | NEW | 1540-TI-4827 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4828 | NEW | 1540-TW-4828 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4828 | NEW | 1540-TE-4828 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4828 | NEW | 1540-TIT-4828 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4828 | NEW | 1540-TI-4828 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4828 | NEW | 1540-TAL-4828 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4828 | NEW | 1540-TAH-4828 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4840 | NEW | 1540-TW-4840 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4840 | NEW | 1540-TE-4840 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4840 | NEW | 1540-TIT-4840 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4840 | NEW | 1540-TI-4840 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4841 | NEW | 1540-TW-4841 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4841 | NEW | 1540-TE-4841 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4841 | NEW | 1540-TIT-4841 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4841 | NEW | 1540-TI-4841 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 2ND PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4842 | NEW | 1540-TW-4842 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4842 | NEW | 1540-TE-4842 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4842 | NEW | 1540-TIT-4842 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4842 | NEW | 1540-TI-4842 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4843 | NEW | 1540-TW-4843 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4843 | NEW | 1540-TE-4843 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4843 | NEW | 1540-TIT-4843 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4843 | NEW | 1540-TI-4843 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 3RD PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4844 | NEW | 1540-TW-4844 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4844 | NEW | 1540-TE-4844 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS UPPER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4844 | NEW | 1540-TIT-4844 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4844 | NEW | 1540-TI-4844 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS UPPER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4845 | NEW | 1540-TW-4845 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4845 | NEW | 1540-TE-4845 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS LOWER BED | ------ | 1540-RE-001 | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4845 | NEW | 1540-TIT-4845 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4845 | NEW | 1540-TI-4845 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 4TH PASS LOWER BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TW-4822 | THERMOWELL | 1540-PR-PID-0000-EXP-5048 | PGS FROM HP SH 1B TO 2ND PASS | 78"-SOX-1540-2118-304SS-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TE-4822 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5048 | PGS FROM HP SH 1B TO 2ND PASS | 78"-SOX-1540-2118-304SS-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TIT-4822 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5048 | PGS FROM HP SH 1B TO 2ND PASS | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TIC-4822 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5048 | PGS FROM HP SH 1B TO 2ND PASS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TAL-4822 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | PGS FROM HP SH 1B TO 2ND PASS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TAH-4822 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | PGS FROM HP SH 1B TO 2ND PASS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4851 | NEW | 1540-PDIT-4851 | PRESSURE TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS BED | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4851 | NEW | 1540-PDI-4851 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | CONV 1ST PASS BED | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4851 | NEW | 1540-FI-4851A | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5048 | HIGH SIDE PURGE FOR PDIT-4851 | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-4851 | NEW | 1540-FI-4851B | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5048 | LOW SIDE PURGE FOR PDIT-4851 | ------ | 1540-RE-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4882 | NEW | 1540-AE-4882 | SO2 AREA MONITOR SENSOR | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4882 | NEW | 1540-AIT-4882 | SO2 AREA MONITOR | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4882 | NEW | 1540-AAI-4882 | DCS INDICATION | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4882 | NEW | 1540-AAHH-4882 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4882 | NEW | 1540-AAH-4882 | DCS ALARM | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-4882 | NEW | 1540-ASH-4882 | INTLK | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-4882A | NEW | 1540-XA-4882A | ALARM BEACON | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-4882B | NEW | 1540-XA-4882B | ALARM HORN | 1540-PR-PID-0000-EXP-5048 | 1540-RE-001 CONV | ------ | 1540-RE-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5231 | NEW | 1540-TW-5231 | THERMOWELL | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 3 TO CIP HEAT EXCH. | 78"-SOX-1540-2114-304SS-HC- | 1540-HX-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5231 | NEW | 1540-TE-5231 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 3 TO CIP HEAT EXCH. | 78"-SOX-1540-2114-304SS-HC- | 1540-HX-008 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5231 | NEW | 1540-TIT-5231 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 3 TO CIP HEAT EXCH. | ------ | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5231 | NEW | 1540-TI-5231 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 3 TO CIP HEAT EXCH. | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5202 | NEW | 1540-PIT-5202 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. PGS INLET | 78"-SOX-1540-2114-304SS-HC- | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5202 | NEW | 1540-PI-5202 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. PGS INLET | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5202 | NEW | 1540-FI-5202 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5202 | ------ | 1540-HX-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5232 | NEW | 1540-TW-5232 | THERMOWELL | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 2 TO HIP HEAT EXCH. | 84"-SOX-1540-2113-30HSS-HC- | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5232 | NEW | 1540-TE-5232 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 2 TO HIP HEAT EXCH. | 84"-SOX-1540-2113-30HSS-HC- | 1540-HX-009 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5232 | NEW | 1540-TIT-5232 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 2 TO HIP HEAT EXCH. | ------ | 1540-HX-009 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5232 | NEW | 1540-TI-5232 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM CONV PASS 2 TO HIP HEAT EXCH. | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5200 | NEW | 1540-PIT-5200 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH PGS INLET | 84"-SOX-1540-2113-304SS-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5200 | NEW | 1540-PI-5200 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH PGS INLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5200 | NEW | 1540-FI-5200 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5200 | ------ | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5201 | NEW | 1540-PIT-5201 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH. PGS OUTLET | 78"-SOX-1540-2119-304SS-HC- | 1540-HX-009 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5201 | NEW | 1540-PI-5201 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH. PGS OUTLET | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5201 | NEW | 1540-FI-5201 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5201 | ------ | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TW-5220 | THERMOWELL | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | 78"-SOX-1540-2119-304SS-HC- | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TE-5220 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | 78"-SOX-1540-2119-304SS-HC- | 1540-HX-009 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TIT-5220 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | ------ | 1540-HX-009 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TIC-5220 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TAL-5220 | DCS ALARM | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TAH-5220 | DCS ALARM | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TCV-5220 | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | 48"-SOX-1540-2122-304SS-HC- | 1540-HX-009 | EXP | NA | NA | NA | NA | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-TY-5220 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5052 | HIP HEAT EXCH BYPASS | ------ | 1540-HX-009 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5220 | NEW | 1540-FI-5220 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR TCV-5220 | ------ | 1540-HX-009 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-5210 | NEW | 1540-BV-5210 | MANUAL DAMPER | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP TO HIP HEAT EXCH. | 72"-SOX-1540-2121-304SS-HC- | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-B-5210 | NEW | 1540-FI-5207 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR BV-5210 | ------ | 1540-HX-009 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5223 | NEW | 1540-TW-5223 | THERMOWELL | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP HEAT EXCH TO HIP HEAT EXCH INLET | 72"-SOX-1540-2121-304SS-HC- |  | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5223 | NEW | 1540-TE-5223 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP HEAT EXCH TO HIP HEAT EXCH INLET | 72"-SOX-1540-2121-304SS-HC- |  | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5223 | NEW | 1540-TIT-5223 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP HEAT EXCH TO HIP HEAT EXCH INLET | ------ |  | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5223 | NEW | 1540-TI-5223 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP HEAT EXCH TO HIP HEAT EXCH INLET | ------ |  | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5206 | NEW | 1540-FI-5206 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5206 | ------ | 1540-HX-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5206 | NEW | 1540-PIT-5206 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP TO HIP HEAT EXCH. | 72"-SOX-1540-2121-304SS-HC- | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5206 | NEW | 1540-PI-5206 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM CIP TO HIP HEAT EXCH. | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5203 | NEW | 1540-FI-5203 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5203 | ------ | 1540-HX-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5203 | NEW | 1540-PIT-5203 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXH. GAS OUTLET | 78"-SOX-1540-2124-304SS-HC- | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5203 | NEW | 1540-PI-5203 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXH. GAS OUTLET | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-5240 | NEW | 1540-LIT-5240 | LEVEL TRANSMITTER - GWR | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. CATCH POT | ------ | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-5240 | NEW | 1540-LI-5240 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. CATCH POT | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-5240 | NEW | 1540-LAH-5240 | DCS ALARM | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. CATCH POT | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-5241 | NEW | 1540-LIT-5241 | LEVEL TRANSMITTER - GWR | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH PGS FROM IPAT CATCH POT | ------ | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-5241 | NEW | 1540-LI-5241 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH PGS FROM IPAT CATCH POT | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-5241 | NEW | 1540-LAH-5241 | DCS ALARM | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH PGS FROM IPAT CATCH POT | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5204 | NEW | 1540-FI-5204 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5204 | ------ | 1540-HX-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5204 | NEW | 1540-PIT-5204 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. PGS FROM IPAT | 72"-SOX-1520-2189-304LSS-HC- | 1540-HX-008 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5204 | NEW | 1540-PI-5204 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | CIP HEAT EXCH. PGS FROM IPAT | ------ | 1540-HX-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5205 | NEW | 1540-FI-5205 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR PIT-5205 | ------ | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5205 | NEW | 1540-PIT-5205 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH TO CONV. PASS 4 | 78"-SOX-1540-2120-304SS-HC- | 1540-HX-009 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-5205 | NEW | 1540-PI-5205 | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH TO CONV. PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TW-5224 | THERMOWELL | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | 78"-SOX-1540-2120-304SS-HC- | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TE-5224 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | 78"-SOX-1540-2120-304SS-HC- | 1540-HX-009 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TIT-5224 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-HS-5224 | DCS OPERATOR INITIATED CONTROL | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TIC-5224 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TAH-5224 | DCS ALARM | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TAL-5224 | DCS ALARM | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TY-5224A | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TY-5224B | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-FI-5224A | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR TCV-5224A | ------ | 1540-HX-009 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TCV-5224A | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | 36"-SOX-1540-2123-304LSS-HC- | 1540-HX-009 | EXP | NA | NA | NA | NA | FLD-INLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-FI-5224B | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5052 | PURGE FOR TCV-5224B | ------ | 1540-HX-009 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-5224 | NEW | 1540-TCV-5224B | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | 72"-SOX-1520-2189-304LSS-HC- | 1540-HX-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224A | NEW | 1540-ZSO-5224A | PART OF VALVE LIMIT SWITCH | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224A | NEW | 1540-ZAO-5224A | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224A | NEW | 1540-ZSC-5224A | PART OF VALVE LIMIT SWITCH | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224A | NEW | 1540-ZAC-5224A | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 | ------ | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224B | NEW | 1540-ZSO-5224B | PART OF VALVE LIMIT SWITCH | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 |  | 1540-HX-009 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224B | NEW | 1540-ZAO-5224B | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 |  | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224B | NEW | 1540-ZSC-5224B | PART OF VALVE LIMIT SWITCH | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 |  | 1540-HX-009 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-5224B | NEW | 1540-ZAC-5224B | DCS INDICATION | 1540-PR-PID-0000-EXP-5052 | PGS FROM HIP HEAT EXCH . TO CONV PASS 4 |  | 1540-HX-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5820 | NEW | 1520-TW-5820 | THERMOWELL | 1520-PR-PID-0000-EXP-5058 | DT SA OUTLET TEMPERATURE | 20"-ACC-1520-2131-CBJ-- | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5820 | NEW | 1520-TE-5820 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5058 | DT SA OUTLET TEMPERATURE | 20"-ACC-1520-2131-CBJ-- | 1520-TW-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5820 | NEW | 1520-TIT-5820 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | DT SA OUTLET TEMPERATURE | ------ | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-5820 | NEW | 1520-TI-5820 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | DT SA OUTLET TEMPERATURE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5801 | NEW | 1520-PIT-5801 | PRESSURE TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT OUTLET | 96"-SOX-1520-2100-304SS-- | 1520-FL-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-5801 | NEW | 1520-PI-5801 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT OUTLET | ------ | 1520-FL-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5801 | NEW | 1520-PAL-5801 | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT OUTLET | ------ | 1520-FL-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5800 | NEW | 1520-PDIT-5800 | VENDOR SUPPLY PRESSURE TRANSMITTER - D/P | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT D/P | ------ | 1520-FL-001 | Vendor | DCS | AI-HART | DCS | 4-20mA HART | FLD-INLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-5800 | NEW | 1520-PDI-5800 | VENDOR SUPPLY PRESSURE GAUGE - D/P | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT D/P | ------ | 1520-FL-001 | Vendor | DCS | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5800 | NEW | 1520-PDI-5800B | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT D/P | ------ | 1520-FL-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5800B | NEW | 1520-PDAH-5800B | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | INLET AIR FLT D/P | ------ | 1520-FL-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-5871 | NEW | 1520-FI-5871A | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | DT LEVEL | ------ | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-5871 | NEW | 1520-FI-5871B | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | DT LEVEL | ------ | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-5871 | NEW | 1520-LIT-5871 | BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | DT LEVEL | ------ | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-L-5871 | NEW | 1520-LI-5871 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | DT LEVEL | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-5871 | NEW | 1520-LAH-5871 | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | DT LEVEL | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TW-5823 | THERMOWELL | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET TEMP | 14"-ACC-1520-2133-CBJ-- | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TE-5823 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET TEMP | 14"-ACC-1520-2133-CBJ-- | 1520-TW-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TIT-5823 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET TEMP | ------ | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TIC-5823 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET TEMP | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TY-5823 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5067 | DT ACID INLET TEMP | ------ | 1520-TW-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TCV-5823 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5067 | DT ACID INLET TEMP | 12"-ACC-1520-9422-CBJ-- | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TAL-5823 | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET TEMP | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5823 | NEW | 1520-TAH-5823 | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET TEMP | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-5870 | NEW | 1520-FE-5870 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET FLOW | 14"-ACC-1520-2133-CBJ-- | 1520-TW-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-5870 | NEW | 1520-FIT-5870 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET FLOW | ------ | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-F-5870 | NEW | 1520-FIC-5870 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET FLOW | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-5870 | NEW | 1520-FSLL-5870 | INTLK | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET FLOW | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-5870 | NEW | 1520-FY-5870 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET FLOW | ------ | 1520-TW-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-F-5870 | NEW | 1520-FCV-5870 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5058 | DT ACID INLET FLOW | 14"-ACC-1520-2133-CBJ-- | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5804 | NEW | 1520-PIT-5804 | PRESSURE TRANSMITTER - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5058 | PGS FROM DT TO MAIN COMP. | 96"-SOX-1520-2101-316LSS-HC- | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-5804 | NEW | 1520-PI-5804 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | PGS FROM DT TO MAIN COMP. | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-5804 | NEW | 1520-PSLL-5804 | INTLK | 1520-PR-PID-0000-EXP-5058 | PGS FROM DT TO MAIN COMP. |  | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-XV-5805 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | 6"-SOX-1520-2128-SBQ-- | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-XEV-5805 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | ------ | 1520-TW-001 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-HS-5805 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-ZSC-5805 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-ZAC-5805 | INTLK | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-ZSO-5805 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-5805 | NEW | 1520-ZAO-5805 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | HIGH POINT VENT TO ATMOSPHERE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5821 | NEW | 1520-TW-5821 | THERMOWELL | 1520-PR-PID-0000-EXP-5058 | DT PGS OUTLET | 96"-SOX-1520-2101-316LSS-HC- | 1520-TW-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5821 | NEW | 1520-TE-5821 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5058 | DT PGS OUTLET | 96"-SOX-1520-2101-316LSS-HC- | 1520-TW-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-5821 | NEW | 1520-TIT-5821 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5058 | DT PGS OUTLET | ------ | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-5821 | NEW | 1520-TI-5821 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | DT PGS OUTLET | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-5842 | NEW | 1520-AE-5842 | SO2 AREA MONITOR SENSOR | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-5842 | NEW | 1520-AIT-5842 | SO2 AREA MONITOR | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-5842 | NEW | 1520-AI-5842 | DCS INDICATION | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-5842 | NEW | 1520-AAHH-5842 | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-5842 | NEW | 1520-AAH-5842 | DCS ALARM | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-5842 | NEW | 1520-ASH-5842 | INTLK | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-5842A | NEW | 1520-XA-5842A | ALARM BEACON | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-5842B | NEW | 1520-XA-5842B | ALARM HORN | 1520-PR-PID-0000-EXP-5058 | 1520-TW-001 DT SO2 AREA MOMITOR | ------ | 1520-TW-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-6001 | NEW | 1520-PI-6001 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5060 | DT ACID PUMP DISCH | 2"-ACC-1520-9491-CBJ-FP-ET | 1520-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-R-6001 | NEW | 1520-RO-6001 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5060 | SA DRAIN PUMP | 4"-ACC-1520-2165-SBQ-FP-ET | 1520-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6003 | NEW | 1520-PI-6003 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5060 | FAT ACID PUMP DISCH | 2"-ACC-1520-9499-CBJ-FP-ET | 1520-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-R-6020 | NEW | 1520-RO-6020 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5060 | DT ACID PUMP RECYCLE | 3"-ACC-1520-9419-CBJ-FP- | 1520-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6022 | NEW | 1520-RO-6022 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5060 | FAT ACID PUMP RECYCLE | 3"-ACC-1520-9421-CBJ-FP-ET | 1520-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AE-6060 | ANALYZER SENSOR - SONIC CONC | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | 1"-ACC-1520-2144-CBJ-FP-ET | 1520-PP-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AIT-6060 | ANALYZER TRANSMITTER - SONIC CONC | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AIC-6060 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AAH-6060 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AAL-6060 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AALL-6060 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-ASLL-6060 | INTLK | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-AY-6060 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | ------ | 1520-PP-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-6060 | NEW | 1520-ACV-6060 | CONTROL VALVE | 1520-PR-PID-0000-EXP-5060 | DT ACID CONC | 2"-TRW-1520-0233-SBA-FP-ET | 1520-PP-001 | 5009 | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-R-6061 | NEW | 1520-RO-6061 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5060 | DT ACID SAMPLE | 1"-ACC-1520-2142-CBJ-FP-ET | 1520-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6062 | NEW | 1520-RO-6062 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5060 | FAT ACID SAMPLE | 1"-ACC-1520-2149-CBJ-FP-ET | 1520-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AE-6063 | ANALYZER SENSOR - SONIC CONC | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | 1"-ACC-1520-2151-CBJ-FP-ET | 1520-PP-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AIT-6063 | ANALYZER TRANSMITTER - SONIC CONC | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AIC-6063 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AAH-6063 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AAL-6063 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AALL-6063 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-ASLL-6063 | INTLK | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-AY-6063 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | ------ | 1520-PP-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6063 | NEW | 1520-ACV-6063 | CONTROL VALVE | 1520-PR-PID-0000-EXP-5060 | FAT ACID CONC | 1"-TRW-1560-2146-SBA-FP-ET | 1520-PP-002 | 5010 | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6064 | NEW | 1520-FE-6064 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5060 | DT ACID SAMPLE | 1"-ACC-1520-2142-CBJ-FP-ET | 1520-PP-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6064 | NEW | 1520-FIT-6064 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5060 | DT ACID SAMPLE | ------ | 1520-PP-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6064 | NEW | 1520-FI-6064 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT ACID SAMPLE | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6064 | NEW | 1520-FAL-6064 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | DT ACID SAMPLE | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6065 | NEW | 1520-FE-6065 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5060 | FAT ACID SAMPLE | 1"-ACC-1520-2149-CBJ-FP-ET | 1520-PP-002 | EXP | NA | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6065 | NEW | 1520-FIT-6065 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5060 | FAT ACID SAMPLE | ------ | 1520-PP-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6065 | NEW | 1520-FI-6065 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT ACID SAMPLE | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6065 | NEW | 1520-FAL-6065 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | FAT ACID SAMPLE | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6070 | NEW | 1520-FE-6070 | FLOW ELEMENT - VORTEX | 1520-PR-PID-0000-EXP-5060 | DT ACID DILUTION WATER | 2"-TRW-1520-0233-SBA-FP-ET | 1520-TK-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6070 | NEW | 1520-FIT-6070 | FLOW TRANSMITTER - VORTEX | 1520-PR-PID-0000-EXP-5060 | DT ACID DILUTION WATER | ------ | 1520-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6070 | NEW | 1520-FI-6070 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT ACID DILUTION WATER | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6070 | NEW | 1520-FSH-6070 | INTLK | 1520-PR-PID-0000-EXP-5060 | DT ACID DILUTION WATER | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6070 | NEW | 1560-FE-6070 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5165 | HP STEAM HEADER | 6"-HPS-1560-6110-AEA-HC- | 1520-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-F-6070 | NEW | 1560-FIT-6070 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5165 | HP STEAM HEADER | ------ | 1520-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1520-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6070 | NEW | 1560-FI-6070 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | HP STEAM HEADER | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6060 | NEW | 1560-FE-6060 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5165 | BYPASS COND PUMPS | 2"-BFW-1560-4129-CEA-HC- | 1520-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-F-6060 | NEW | 1560-FIT-6060 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5165 | BYPASS COND PUMPS | ------ | 1520-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1520-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6060 | NEW | 1560-FI-6060 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | BYPASS COND PUMPS | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6040 | NEW | 1560-FE-6040 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5165 | BYPASS COND PUMPS | 2"-BFW-1560-6115-CEA-HC- | 1520-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-F-6040 | NEW | 1560-FIT-6040 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5165 | BYPASS COND PUMPS | ------ | 1520-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1520-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6040 | NEW | 1560-FI-6040 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | BYPASS COND PUMPS | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-ZSC-6071 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-ZAC-6071 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-ZSO-6071 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-ZAO-6071 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-HS-6071 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-XEV-6071 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-PP-001 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6071 | NEW | 1520-XV-6071 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | 2"-TRW-1520-0233-SBA-FP-ET | 1520-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-ZSC-6072 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-ZAC-6072 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-ZSO-6072 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-ZAO-6072 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-HS-6072 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-XEV-6072 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | ------ | 1520-PP-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6072 | NEW | 1520-XV-6072 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5060 | FAT ACID DILUTION BLOCK VALVE | 1"-TRW-1520-2146-SBA-FP-ET | 1520-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-XEV-6080 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-PP-001 | EXP | DCS | DO | RIO | DO | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-XV-6080 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | 2"-TRW-1520-0233-SBA-FP-ET | 1520-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-ZSC-6080 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-ZAC-6080 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-ZSO-6080 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-ZAO-6080 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6080 | NEW | 1520-HS-6080 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-ZSC-6081 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-ZAC-6081 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-ZSO-6081 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-ZAO-6081 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-HS-6081 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-XEV-6081 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6081 | NEW | 1520-XV-6081 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5060 | DT DILUTION WATER BLEED VALVE | 1"-TRW-1520-2145-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-ZSC-6082 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-ZAC-6082 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-ZSO-6082 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-ZAO-6082 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-HS-6082 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-XEV-6082 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6082 | NEW | 1520-XV-6082 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLEED VALVE | 1"-TRW-1520-2147-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-ZSC-6083 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-ZAC-6083 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-ZSO-6083 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-ZAO-6083 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-HS-6083 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | ------ | 1520-TW-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-XEV-6083 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6083 | NEW | 1520-XV-6083 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER BLOCK VALVE | 1"-TRW-1520-2146-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-H-6090 | NEW | 1520-HS-6090 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5060 | DT/IPAT ACID PUMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-6091 | NEW | 1520-HS-6091 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5060 | FAT PUMP | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-F-6074 | NEW | 1520-FE-6074 | FLOW ELEMENT - VORTEX | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER | 1"-TRW-1520-2146-SBA-FP-ET | 1520-PP-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6074 | NEW | 1520-FIT-6074 | FLOW TRANSMITTER - VORTEX | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER | ------ | 1520-PP-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6074 | NEW | 1520-FI-6074 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6074 | NEW | 1520-FSH-6074 | INTLK | 1520-PR-PID-0000-EXP-5060 | FAT DILUTION WATER | ------ | 1520-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6093 | NEW | 1520-LIT-6093 | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5060 | SA AREA SUMP | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6093 | NEW | 1520-LI-6093 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | SA AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6093 | NEW | 1520-LAH-6093 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | SA AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LIT-6040A | LEVEL TRANSMITTER - GWR | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LI-6040A | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LALL-6040A | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LY-6040A | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5067 | CPT LEVEL | ------ | 1520-TK-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LCV-6040A | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5067 | SA TO DILUTION PUMP TK | 6"-ACC-1520-2134-CBJ-- | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LIT-6040B | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LI-6040B | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LALL-6040B | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-FI-6040B | FLOW GAUGE - ROTAMETER | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-HS-6040 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LIC-6040 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LAHH-6040 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LAH-6040 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LAL-6040 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LALL-6040 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LSLL-6040 | INTLK | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6040 | NEW | 1520-LSHH-6040 | INTLK | 1520-PR-PID-0000-EXP-5060 | CPT LEVEL | ------ | 1520-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6031 | NEW | 1520-TE-6031 | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP WINDING TEMP | ------ | 1520-PP-001 | Vendor | N/A | AI-W | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6031 | NEW | 1520-TI-6031 | DCS INDICATION | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP WINDING TEMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6031 | NEW | 1520-TI-6031 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP WINDING TEMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | PLC | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6031 | NEW | 1520-TAH-6031 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP WINDING TEMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-6030 | NEW | 1520-VS-6030 | VENDOR SUPPLY VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP | ------ | 1520-PP-001 | EXP | DCS | DI | DCS | 24V | DCS | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-6030 | NEW | 1520-VAHH-6030 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-6030 | NEW | 1520-VAH-6030 | DCS ALARM | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-6030 | NEW | 1520-VAH-6030 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5060 | 1520-PP-001 DT/IT ACID PUMP | ------ | 1520-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1560 | STRONG ACID | 1560-R-6201 | NEW | 1560-RO-6201 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5162 | TURBINE EXTERNAL DRAIN | 3/4"-HCD-1560-9622-AEA-PP- | 1560-TG-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6200 | NEW | 1560-XS-6200 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TURBINE TRIP TO DCS | ------ | 1560-TG-001 | EXP | PLC | DI-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6201 | NEW | 1560-XS-6201 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TURBINE SPEED | ------ | 1560-TG-001 | EXP | PLC | DI-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6202 | NEW | 1560-XS-6202 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | SIGNAL TO BYPASS PROTECTION | ------ | 1560-TG-001 | EXP | PLC | DI-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6203 | NEW | 1560-XS-6203 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | SIGNAL TO BYPASS PROTECTION | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6317 | NEW | 1560-PIA-6317 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | SIGNAL TO BYPASS PROTECTION | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6204 | NEW | 1560-XS-6204 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | SIGNAL TO BYPASS PROTECTION | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6232 | NEW | 1560-TIA-6232 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | SIGNAL TO BYPASS PROTECTION | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6211 | NEW | 1560-XS-6211 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | FIRE PROTECTION SIGNAL | ------ | 1560-TG-001 | EXP | PLC | DI-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6210 | NEW | 1560-XS-6210 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5160 | DCS REMOTE TRIP | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6210 | NEW | 1520-PI-6210 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5062 | PROCUCT ACID PUMP DISCH | 2"-ACC-1520-2169-CBQ-FP- | 1520-PP-005 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LIT-6240 | LEVEL TRANSMITTER - GWR | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LIC-6240 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LI-6240 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LAL-6240 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LAH-6240 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LAHH-6240 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LALL-6240 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LSHH-6240 | INTLK | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LSLL-6240 | INTLK | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LY-6240 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5064 | PROD ACID TO STOR | ------ | 1570-TK-001/002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6240 | NEW | 1520-LCV-6240 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5064 | PROD ACID TO STOR | 6"-ACC-1520-2167-SBQ-- | 1570-TK-001/002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-6240 | NEW | 1520-HS-6240 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5062 | PROD ACID TO STOR | ------ | 1570-TK-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-LIT-6241 | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-LI-6241 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-LALL-6241 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-LAHH-6241 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-LSLL-6241 | INTLK | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-LSHH-6241 | INTLK | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6241 | NEW | 1520-FI-6241 | FLOW GAUGE - ROTAMETER | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK LEVEL | ------ | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6242 | NEW | 1520-FE-6242 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5062 | PROD ACID PUMP RECIRC | 1"-ACC-1520-2157-CBQ-FP-ET | 1520-PP-005 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6242 | NEW | 1520-FIT-6242 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5062 | PROD ACID PUMP RECIRC | ------ | 1520-PP-005 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6242 | NEW | 1520-FI-6242 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | PROD ACID PUMP RECIRC | ------ | 1520-PP-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AE-6260 | ANALYZER SENSOR - SONIC CONC | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | 1"-ACC-1520-2159-CBQ-FP-ET | 1520-TK-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AIT-6260 | ANALYZER TRANSMITTER - SONIC CONC | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | ------ | 1520-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AIC-6260 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AAL-6260 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AAH-6260 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AALL-6260 | DCS ALARM | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC |  | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-ASLL-6260 | INTLK | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-AY-6260 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | ------ | 1520-TK-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6260 | NEW | 1520-ACV-6260 | CONTROL VALVE | 1520-PR-PID-0000-EXP-5062 | PROD ACID CONC | 1-1/2"-TRW-1520-0244-SBA-FP-ET | 1520-TK-002 | 5011 | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-R-6261 | NEW | 1520-RO-6261 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK SA INLET | 6"-ACC-1520-2162-CBQ-FP- | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6262 | NEW | 1520-RO-6262 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5062 | DILUTION PUMP TK SA INLET | 1"-ACC-1520-2157-CBQ-FP-ET | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6270 | NEW | 1520-FE-6270 | FLOW ELEMENT - VORTEX | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK | 1-1/2"-TRW-1520-0244-SBA-FP-ET | 1520-TK-002 | EXP | DCS | NA | N/A | mV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-6270 | NEW | 1520-FIT-6270 | FLOW TRANSMITTER - VORTEX | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK | ------ | 1520-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2701 | NEW | 1560-FE-2701 | FLOW ELEMENT - VORTEX | 1560-PR-PID-0000-EXP-5127 | TW PUMPS TO RO MEMBRANE | 3"-TRW-1560-9801-SBA-FP- | N/A | EXP | DCS | NA | N/A | mV | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-F-2701 | NEW | 1560-FIT-2701 | FLOW TRANSMITTER - VORTEX | 1560-PR-PID-0000-EXP-5127 | TW PUMPS TO RO MEMBRANE | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2701 | NEW | 1560-FIC-2701 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5127 | TW PUMPS TO RO MEMBRANE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2701 | NEW | 1560-FY-2701 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5127 | TW PUMPS TO RO MEMBRANE | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1520-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2701 | NEW | 1560-FCV-2701 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5127 | TW PUMPS TO RO MEMBRANE | 3"-TRW-1560-9801-SBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6270 | NEW | 1520-FSH-6270 | INTLK | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6270 | NEW | 1520-FI-6270 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-XEV-6280 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-XV-6280 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | 1-1/2"-TRW-1520-0244-SBA-FP-ET | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-ZSC-6280 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-ZSO-6280 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-ZAC-6280 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-ZAO-6280 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6280 | NEW | 1520-HS-6280 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6281 | NEW | 1520-XEV-6281 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | ------ | 1520-TK-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6281 | NEW | 1520-XV-6281 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | 1"-TRW-1520-2155-SBA-FP-ET | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-Z-6281 | NEW | 1520-ZSC-6281 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | ------ | 1520-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-Z-6281 | NEW | 1520-ZSO-6281 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | ------ | 1520-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-Z-6281 | NEW | 1520-ZAC-6281 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-Z-6281 | NEW | 1520-ZAO-6281 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-6281 | NEW | 1520-HS-6281 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLEED VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-XEV-6282 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-XV-6282 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | 1-1/2"-TRW-1520-0244-SBA-FP-ET | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-ZSC-6282 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-ZSO-6282 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-ZAC-6282 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-ZAO-6282 | DCS INDICATION | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6282 | NEW | 1520-HS-6282 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5062 | DILUTION WATER TO DILUTION PUMP TK BLOCK VALVE | ------ | 1520-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-6290 | NEW | 1520-HS-6290 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5062 | PROD ACID PUMP | ------ | 1520-PP-005 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-J-6490 | NEW | 1520-JI-6490 | POWER MONITOR | 1520-PR-PID-0000-EXP-5064 | SA DRAIN PUMP POWER MONITOR | ------ | 1520-PP-007 | EXP | DCS | SOFTWARE | DCS | SOFT | MCC | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-6490 | NEW | 1520-HS-6490 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5064 | SA DRAIN PUMP START/STOP | ------ | 1520-PP-007 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-P-6413 | NEW | 1520-PI-6413 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER SA INLET | 2"-ACC-1520-9493-CBQ-FP- | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6201 | NEW | 1520-RO-6201 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5062 | TURBINE EXTERNAL DRAIN | 3/4"-HCD-1560-9622-AEA-PP- | 1560-TG-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6415 | NEW | 1520-RO-6415 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5064 | CW SUPPLY TO PROD ACID COOLER | 8"-CLW-1520-5112-CBA-- | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6433 | NEW | 1520-TW-6433 | THERMOWELL | 1520-PR-PID-0000-EXP-5064 | CW SUPPLY TO PROD ACID COOLER | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6433 | NEW | 1520-TI-6433 | TEMPERATURE GAUGE | 1520-PR-PID-0000-EXP-5064 | CW SUPPLY TO PROD ACID COOLER | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6418 | NEW | 1520-PI-6418 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5064 | PRODUCT ACID COOLER COOLING WATER OUTLET | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6416 | NEW | 1520-PI-6416 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5064 | CW SUPPLY TO PROD ACID COOLER | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6411 | NEW | 1520-PI-6411 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER SA INLET | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6420 | NEW | 1520-TW-6420 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER OUTLET | ------ | 1520-CO-003 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6420 | NEW | 1520-TE-6420 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER OUTLET | ------ | 1520-CO-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6420 | NEW | 1520-TIT-6420 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER OUTLET | ------ | 1520-CO-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6420 | NEW | 1520-TI-6420 | DCS INDICATION | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER OUTLET | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6420 | NEW | 1520-TAH-6420 | DCS ALARM | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER OUTLET | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6421 | NEW | 1520-TW-6421 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER INLET | ------ | 1520-CO-003 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6421 | NEW | 1520-TE-6421 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER INLET | ------ | 1520-CO-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6421 | NEW | 1520-TIT-6421 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER INLET | ------ | 1520-CO-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6421 | NEW | 1520-TI-6421 | DCS INDICATION | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER INLET | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6421 | NEW | 1520-TAH-6421 | DCS ALARM | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER INLET | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6412 | NEW | 1520-PI-6412 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER SA OUTLET | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6434 | NEW | 1520-TW-6434 | THERMOWELL | 1520-PR-PID-0000-EXP-5064 | CW RETURN FROM PROD ACID COOLER | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6434 | NEW | 1520-TI-6434 | TEMPERATURE GAUGE | 1520-PR-PID-0000-EXP-5064 | CW RETURN FROM PROD ACID COOLER | ------ | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6481 | NEW | 1520-PSV-6481 | PRESSURE RELIEF VALVE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CW RETURN | 2"-CLW-1520-6144-CBA-- | 1520-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6461 | NEW | 1520-AE-6461 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CW RETURN | 8"-CLW-1520-2371-CBA-- | 1520-CO-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6461 | NEW | 1520-AIT-6461 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CW RETURN | ------ | 1520-CO-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6461 | NEW | 1520-AI-6461 | DCS INDICATION | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CW RETURN | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6461 | NEW | 1520-AAH-6461 | DCS ALARM | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CW RETURN | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6462 | NEW | 1520-XA-6462 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER ANODIC PROTECTION | ------ | 1520-CO-003 | EXP | DCS | DI-S | PLC | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-F-6470 | NEW | 1520-FE-6470 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5064 | PROD ACID TO STOR | 6"-ACC-1520-2167-SBQ-- | 1570-TK-001/002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6470 | NEW | 1520-FIT-6470 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5064 | PROD ACID TO STOR | ------ | 1570-TK-001/002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6470 | NEW | 1520-FI-6470 | DCS INDICATION | 1520-PR-PID-0000-EXP-5064 | PROD ACID TO STOR | ------ | 1570-TK-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6470 | NEW | 1520-FQI-6470 | DCS TOTALIZATION | 1520-PR-PID-0000-EXP-5064 | PROD ACID TO STOR | ------ | 1570-TK-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6410 | NEW | 1520-PI-6410 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5064 | SADRAIN PUMP DISCH | 4"-ACC-1520-2166-SBQ-FP-ET | 1520-PP-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-E-6486 | NEW | 1520-EI-6486 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CATH VOLTAGE | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6485 | NEW | 1520-EI-6485 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER AUX3 REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-I-6482 | NEW | 1520-II-6482 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CATH CURRENT | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6481 | NEW | 1520-XS-6481 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CATH RELAY | ------ | 1520-CO-003 | EXP | DCS | DO | DCS | 24V | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6484 | NEW | 1520-EI-6484 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER AUX1 REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6480 | NEW | 1520-EI-6480 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CTRL REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6480 | NEW | 1520-XIC-6480 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER CTRL SIG | ------ | 1520-CO-003 | EXP | DCS | AO | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-H-6480 | NEW | 1520-HS-6480 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5064 | PROD ACID COOLER | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6521 | NEW | 1520-TW-6521 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER SA OUTLET | ------ | 1520-CO-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6521 | NEW | 1520-TE-6521 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER SA OUTLET | ------ | 1520-CO-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6521 | NEW | 1520-TIT-6521 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER SA OUTLET | 0-300-0-300-F-- | 1520-CO-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6521 | NEW | 1520-TI-6521 | DCS INDICATION | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER SA OUTLET | ------ | 1520-CO-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6510 | NEW | 1520-PI-6510 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER SA OUTLET | 2"-ACC-1520-9503-CBJ-FP- | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6553 | NEW | 1520-TW-6553 | THERMOWELL | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW INLET | ------ | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6553 | NEW | 1520-TI-6553 | TEMPERATURE GAUGE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW INLET | ------ | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6551 | NEW | 1520-PI-6551 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW INLET | ------ | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6550 | NEW | 1520-RO-6550 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW INLET | 10"-CLW-1520-2359-CBA-- | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6512 | NEW | 1520-TW-6512 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER ACID INLET | ------ | 1520-CO-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6512 | NEW | 1520-TE-6512 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER ACID INLET | ------ | 1520-CO-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6512 | NEW | 1520-TIT-6512 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER ACID INLET | ------ | 1520-CO-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6512 | NEW | 1520-TI-6512 | DCS INDICATION | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER ACID INLET | ------ | 1520-CO-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6511 | NEW | 1520-PI-6511 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER SA INTLET | 2"-ACC-1520-9500-CBJ-FP- | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6553 | NEW | 1520-XA-6553 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER ANODIC PROTECTION | ------ | 1520-CO-002 | Vendor | DCS | DI-S | PLC | SOFT | FLD-OFFLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6554 | NEW | 1520-TW-6554 | THERMOWELL | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | ------ | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6554 | NEW | 1520-TI-6554 | TEMPERATURE GAUGE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | ------ | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6552 | NEW | 1520-PI-6552 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | ------ | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6582 | NEW | 1520-PSV-6582 | PRESSURE RELIEF VALVE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | 10"-CLW-1520-2374-CBA-- | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6562 | NEW | 1520-AE-6562 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | 10"-CLW-1520-2374-CBA-- | 1520-CO-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6562 | NEW | 1520-AIT-6562 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | ------ | 1520-CO-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6562 | NEW | 1520-AI-6562 | DCS INDICATION | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | ------ | 1520-CO-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6562 | NEW | 1520-AAH-6562 | DCS ALARM | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CW RETURN | ------ | 1520-CO-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-E-6586 | NEW | 1520-EI-6586 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CATH VOLTAGE | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6585 | NEW | 1520-EI-6585 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER AUX3 REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-I-6582 | NEW | 1520-II-6582 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CATH CURRENT | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6581 | NEW | 1520-XS-6581 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CATH RELAY | ------ | 1520-CO-003 | EXP | DCS | DO | DCS | 24V | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6584 | NEW | 1520-EI-6584 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER AUX1 REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6580 | NEW | 1520-EI-6580 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CTRL REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6580 | NEW | 1520-XIC-6580 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER CTRL SIG | ------ | 1520-CO-003 | EXP | DCS | AO | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-H-6580 | NEW | 1520-HS-6580 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TY-6622 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER BYPASS | ------ | 1520-CO-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TCV-6622 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5065 | FAT ACID COOLER BYPASS | 12"-ACC-1520-2172-CBJ-- | 1520-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FE-6670 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | 14"-ACC-1520-2173-CBJ-- | 1520-TW-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FIT-6670 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | ------ | 1520-TW-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FIC-6670 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FAH-6670 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FAL-6670 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FALL-6670 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET |  | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FSLL-6670 | INTLK | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FY-6670 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | ------ | 1520-TW-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-F-6670 | NEW | 1520-FCV-6670 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5066 | FAT ACID INLET | 14"-ACC-1520-2173-CBJ-- | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6625 | NEW | 1520-LIT-6625 | BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5066 | FAT LEVEL | ------ | 1520-TW-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-6625 | NEW | 1520-LI-6625 | DCS INDICATION | 1520-PR-PID-0000-EXP-5066 | FAT LEVEL | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6625 | NEW | 1520-LAH-6625 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT LEVEL | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6625 | NEW | 1520-FI-6625A | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5066 | HIGH SIDE PURGE FOR LIT-6625 | ------ | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-6625 | NEW | 1520-FI-6625B | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5066 | LOW SIDE PURGE FOR LIT-6625 | ------ | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6623 | NEW | 1520-TW-6623 | THERMOWELL | 1520-PR-PID-0000-EXP-5066 | FAT SA OUTLET | 18"-ACC-1520-2175-CBJ-FP-ET | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6623 | NEW | 1520-TE-6623 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5066 | FAT SA OUTLET | 18"-ACC-1520-2175-CBJ-FP-ET | 1520-TW-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6623 | NEW | 1520-TIT-6623 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5066 | FAT SA OUTLET | ------ | 1520-TW-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6623 | NEW | 1520-TI-6623 | DCS INDICATION | 1520-PR-PID-0000-EXP-5066 | FAT SA OUTLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6624 | NEW | 1520-TW-6624 | THERMOWELL | 1520-PR-PID-0000-EXP-5066 | FAT PGS OUTLET | 72"-SOX-1520-2130-304SS-PP- | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6624 | NEW | 1520-TE-6624 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5066 | FAT PGS OUTLET | 72"-SOX-1520-2130-304SS-PP- | 1520-TW-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6624 | NEW | 1520-TIT-6624 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5066 | FAT PGS OUTLET | ------ | 1520-TW-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6624 | NEW | 1520-TI-6624 | DCS INDICATION | 1520-PR-PID-0000-EXP-5066 | FAT PGS OUTLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6624 | NEW | 1520-TAH-6624 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT PGS OUTLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TW-6622 | THERMOWELL | 1520-PR-PID-0000-EXP-5066 | FAT SA INLET | 14"-ACC-1520-2173-CBJ-- | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TE-6622 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5066 | FAT SA INLET | 14"-ACC-1520-2173-CBJ-- | 1520-TW-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TIT-6622 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5066 | FAT SA INLET | ------ | 1520-TW-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TAH-6622 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT SA INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TAL-6622 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | FAT SA INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6622 | NEW | 1520-TIC-6622 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5066 | FAT SA INLET | ------ | 1520-TW-002 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-HS-6630 | OPERATOR INITIATED DCS CONTROL | 1520-PR-PID-0000-EXP-5066 | FAT VENT | ------ | 1520-TW-002 | EXP | DCS | SOFT | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-XEV-6630 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5066 | FAT VENT | ------ | 1520-TW-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-XV-6630 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5066 | FAT VENT | 6"-SOX-1520-6605-SBL-- | 1520-TW-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-ZAC-6630 | INTLK | 1520-PR-PID-0000-EXP-5066 | FAT VENT | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-ZSC-6630 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5066 | FAT VENT | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-ZAO-6630 | DCS INDICATION | 1520-PR-PID-0000-EXP-5066 | FAT VENT | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6630 | NEW | 1520-ZSO-6630 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5066 | FAT VENT | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6641 | NEW | 1520-AE-6641 | SO2 AREA MONITOR SENSOR | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | NA | E-T | NA | mV | FLD-OFFLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6641 | NEW | 1520-AIT-6641 | SO2 AREA MONITOR | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-6641 | NEW | 1520-AI-6641 | DCS INDICATION | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6641 | NEW | 1520-AAH-6641 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6641 | NEW | 1520-AAHH-6641 | DCS ALARM | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6641 | NEW | 1520-ASH-6641 | INTLK | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6641 | NEW | 1520-XA-6641A | ALARM BEACON | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-6641 | NEW | 1520-XA-6641B | ALARM HORN | 1520-PR-PID-0000-EXP-5066 | 1520-TW-002 FAT | ------ | 1520-TW-002 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-R-6701 | NEW | 1520-RO-6701 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 18"-ACC-1520-6701-CBJ-- | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6702 | NEW | 1520-RO-6702 | STRONG ACID ORIFICE PLATE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 6"-ACC-1520-2134-CBJ-- | 1520-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6753 | NEW | 1520-TW-6753 | THERMOWELL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW INLET | ------ | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6753 | NEW | 1520-TI-6753 | TEMPERATURE GAUGE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW INLET | ------ | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6751 | NEW | 1520-PI-6751 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW INLET | ------ | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-6750 | NEW | 1520-RO-6750 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW INLET | 24"-CLW-1520-1800-CBA-- | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6721 | NEW | 1520-TW-6721 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-006 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6721 | NEW | 1520-TE-6721 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6721 | NEW | 1520-TIT-6721 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6721 | NEW | 1520-TI-6721 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6710 | NEW | 1520-PI-6710 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 2"-ACC-1520-9495-CBJ-FP- | 1520-CO-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6712 | NEW | 1520-TW-6712 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA INLET | ------ | 1520-CO-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6712 | NEW | 1520-TE-6712 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA INLET | ------ | 1520-CO-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6712 | NEW | 1520-TIT-6712 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA INLET | ------ | 1520-CO-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6712 | NEW | 1520-TI-6712 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA INLET | ------ | 1520-CO-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6711 | NEW | 1520-PI-6711 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA INLET | 2"-ACC-1520-9496-CBJ-FP- | 1520-CO-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6754 | NEW | 1520-TW-6754 | THERMOWELL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | ------ | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6754 | NEW | 1520-TI-6754 | TEMPERATURE GAUGE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | ------ | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6752 | NEW | 1520-PI-6752 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | ------ | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6782 | NEW | 1520-PSV-6782 | PRESSURE RELIEF VALVE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | 1"-CLW-1520-6703-CBA-- | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6762 | NEW | 1520-AE-6762 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | 24"-CLW-1520-2963-CBA-- | 1520-CO-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6762 | NEW | 1520-AIT-6762 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | ------ | 1520-CO-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-6762 | NEW | 1520-AI-6762 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | ------ | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6762 | NEW | 1520-AAH-6762 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER CW OUTLET | ------ | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6726 | NEW | 1520-TE-6726 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW OUTLET | ------ | 1520-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6726 | NEW | 1520-TW-6726 | THERMOWELL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW OUTLET | ------ | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6726 | NEW | 1520-TI-6726 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW OUTLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6726 | NEW | 1520-TIT-6726 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW OUTLET | ------ | 1520-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-T-6726 | NEW | 1520-TAH-6726 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW OUTLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6727 | NEW | 1520-PI-6727 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW OUTLET | ------ | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6728 | NEW | 1520-TE-6728 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA INLET | ------ | 1520-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6728 | NEW | 1520-TW-6728 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA INLET | ------ | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6728 | NEW | 1520-TI-6728 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA INLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6728 | NEW | 1520-TIT-6728 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA INLET | ------ | 1520-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-6730 | NEW | 1520-PI-6730 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA INLET | 2"-ACC-1520-9497-CBJ-FP- | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6734 | NEW | 1520-TE-6734 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA OUTLET | ------ | 1520-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6734 | NEW | 1520-TW-6734 | VENDOR SUPPLY THERMOWELL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA OUTLET | ------ | 1520-HX-006 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6734 | NEW | 1520-TI-6734 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA OUTLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6734 | NEW | 1520-TIT-6734 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA OUTLET | ------ | 1520-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-6732 | NEW | 1520-PI-6732 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER SA OUTLET | 2"-ACC-1520-9498-CBJ-FP- | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6736 | NEW | 1520-TE-6736 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6736 | NEW | 1520-TW-6736 | THERMOWELL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6736 | NEW | 1520-TI-6736 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6736 | NEW | 1520-TIT-6736 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-P-6735 | NEW | 1520-PI-6735 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-E-6786 | NEW | 1520-EI-6786 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER CATH VOLTAGE | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6785 | NEW | 1520-EI-6785 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER AUX3 REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-I-6782 | NEW | 1520-II-6782 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER CATH CURRENT | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6781 | NEW | 1520-XS-6781 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER CATH RELAY | ------ | 1520-CO-003 | EXP | DCS | DO | DCS | 24V | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6784 | NEW | 1520-EI-6784 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER AUX1 REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-E-6780 | NEW | 1520-EI-6780 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER CTRL REF | ------ | 1520-CO-003 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6780 | NEW | 1520-XIC-6780 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DT/IT ACID COOLER CTRL SIG | ------ | 1520-CO-003 | EXP | DCS | AO | DCS | 4-20mA | DCS | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-H-6780 | NEW | 1520-HS-6780 | DCS SELECTOR | 1520-PR-PID-0000-EXP-5067 | FAT ACID COOLER | ------ | 1520-CO-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6755 | NEW | 1520-XA-6755 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5067 | DRYING/INTERPASS COOLER ANODIC PROTECTION | ------ | 1520-HX-006 | Vendor | DCS | DI-S | PLC | 24V | FLD-OFFLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FE-6770 | FLOW ELEMENT - MAGNETIC | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 16"-ACC-1520-6701-CBJ-- | 1520-CO-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FIT-6770 | FLOW TRANSMITTER - MAGNETIC | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | 120 VAC/60 Hz | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FIC-6770 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FAH-6770 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET |  | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FAL-6770 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET |  | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FSLL-6770 | INTLK | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET |  | 1520-CO-001 | EXP | DCS | SOFT | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FY-6770 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-F-6770 | NEW | 1520-FCV-6770 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 16"-ACC-1520-6701-CBJ-- | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TE-6722 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 16"-ACC-1520-6701-CBJ-- | 1520-CO-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TW-6722 | THERMOWELL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 16"-ACC-1520-6701-CBJ-- | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TIC-6722 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TIT-6722 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TAH-6722 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TAL-6722 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TY-6722 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | ------ | 1520-CO-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-6722 | NEW | 1520-TCV-6722 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5067 | INTERPASS ACID COOLER SA OUTLET | 14"-ACC-1520-6700-CBJ-- | 1520-CO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TE-6731 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 6"-TRW-1520-2290-SBA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TW-6731 | THERMOWELL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 6"-TRW-1520-2290-SBA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TIC-6731 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TIT-6731 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TAH-6731 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TSHH-6731 | INTLK | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TY-6731 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-6731 | NEW | 1520-TCV-6731 | STRONG ACID CONTROL VALVE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 12"-ACC-1520-9413-CBJ-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-XEV-6741 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-HX-006 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-XV-6741 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 6"-TRW-1520-2290-SBA-HC- | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-HS-6741 | OPERATOR INITIATED DCS CONTROL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-TW-002 | EXP | DCS | SOFT | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-ZAC-6741 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-ZSC-6741 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-ZAO-6741 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6741 | NEW | 1520-ZSO-6741 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-XEV-6742 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5067 | TW HEADER | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-XV-6742 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5067 | TW HEADER | 6"-TRW-1520-2291-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-HS-6742 | OPERATOR INITIATED DCS CONTROL | 1520-PR-PID-0000-EXP-5067 | TW HEADER | ------ | 1520-TW-002 | EXP | DCS | SOFT | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-ZAC-6742 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | TW HEADER | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-ZSC-6742 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | TW HEADER | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-ZAO-6742 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | TW HEADER | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6742 | NEW | 1520-ZSO-6742 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | TW HEADER | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-XEV-6738 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WATER INLET | ------ | 1520-HX-006 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-XV-6738 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | 6"-TRW-1560-0192-SBA-FP- | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-HS-6738 | OPERATOR INITIATED DCS CONTROL | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-TW-002 | EXP | DCS | SOFT | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-ZAC-6738 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-ZSC-6738 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-ZAO-6738 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-TW-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-6738 | NEW | 1520-ZSO-6738 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TW INLET | ------ | 1520-TW-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-A-6745 | NEW | 1520-AE-6745 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 6"-TRW-1520-2290-SBA-HC- | 1520-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6745 | NEW | 1520-AIT-6745 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-6745 | NEW | 1520-AI-6745 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6745 | NEW | 1520-AAH-6745 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6745 | NEW | 1520-ASHH-6745 | INTLK | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | ------ | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-6743 | NEW | 1520-PSV-6743 | PRESSURE RELIEF VALVE | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 6"-TRW-1520-2290-SBA-HC- | 1520-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6746 | NEW | 1520-AE-6746 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET | 6"-TRW-1520-2290-SBA-HC- | 1520-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6746 | NEW | 1520-AIT-6746 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET |  | 1520-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-6746 | NEW | 1520-AI-6746 | DCS INDICATION | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET |  | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6746 | NEW | 1520-AAH-6746 | DCS ALARM | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET |  | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-6746 | NEW | 1520-AASHH-6746 | INTLK | 1520-PR-PID-0000-EXP-5067 | BFW PREHEATER TREATED WT OUTLET |  | 1520-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TW-8421 | THERMOWELL | 1520-PR-PID-0000-EXP-5084 | IPAT PGS TO INTERPASS HEX | 72"-SOX-1520-2189-304LSS-HC- | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TE-8421 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5084 | IPAT PGS TO INTERPASS HEX | 72"-SOX-1520-2189-304LSS-HC- | 1520-TW-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TIT-8421 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5084 | IPAT PGS TO INTERPASS HEX | ------ | 1520-TW-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-8421 | DCS INDICATION | 1520-PR-PID-0000-EXP-5084 | IPAT PGS TO INTERPASS HEX | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TAH-8421 | DCS ALARM | 1520-PR-PID-0000-EXP-5084 | IPAT PGS TO INTERPASS HEX | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-XEV-8423 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | ------ | 1520-TW-003 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-XV-8423 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | 6"-SOX-1520-8402-SBM-- | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-HS-8423 | OPERATOR INITIATED DCS CONTROL | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-ZSC-8423 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-ZAC-8423 | INTLK | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-ZSO-8423 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-8423 | NEW | 1520-ZAO-8423 | DCS INDICATION | 1520-PR-PID-0000-EXP-5084 | IPAT VENT | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8464 | NEW | 1520-TW-8464 | THERMOWELL | 1520-PR-PID-0000-EXP-5084 | IPAT ACID TEMP | 24"-ACC-1520-8400-CBJ-FP-ET | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8464 | NEW | 1520-TE-8464 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5084 | IPAT ACID TEMP | 24"-ACC-1520-8400-CBJ-FP-ET | 1520-TW-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8464 | NEW | 1520-TIT-8464 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5084 | IPAT ACID TEMP | ------ | 1520-TW-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-T-8464 | NEW | 1520-TI-8464 | DCS INDICATION | 1520-PR-PID-0000-EXP-5084 | IPAT ACID TEMP | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-8461 | NEW | 1520-LI-8461 | DCS INDICATION | 1520-PR-PID-0000-EXP-5084 | IPAT ACID LEVEL | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-8461 | NEW | 1520-LAH-8461 | DCS ALARM | 1520-PR-PID-0000-EXP-5084 | IPAT ACID LEVEL | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-8461 | NEW | 1520-LIT-8461 | BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5084 | IPAT ACID LEVEL | ------ | 1520-TW-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-L-8461 | NEW | 1520-FI-8461A | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5084 | HIGH SIDE PURGE FOR LIT-8461 | ------ | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-8461 | NEW | 1520-FI-8461B | ROTAMETER - PART OF BUBBLER LEVEL TRANSMITTER | 1520-PR-PID-0000-EXP-5084 | LOW SIDE PURGE FOR LIT-8461 | ------ | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-XEV-1400 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | ------ | 1520-TK-005 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-XS-1400 | DCS OPERATOR INITIATED CONTROL | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-ZSC-1400 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | ------ | 1520-TK-005 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-ZAC-1400 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-ZSO-1400 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | ------ | 1520-TK-005 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-ZAO-1400 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-1400 | NEW | 1520-XV-1400 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK TW INLET | 2"-TRW-1520-0197-SBA-FP-ET | 1520-TK-005 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-L-1401 | NEW | 1520-LIT-1401 | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK | ------ | 1520-TK-005 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-L-1401 | NEW | 1520-LI-1401 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-1401 | NEW | 1520-LSLL-1401 | INTLK | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-1401 | NEW | 1520-LSL-1401 | INTLK | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-1401 | NEW | 1520-LSH-1401 | INTLK | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW EXPANSION TK | ------ | 1520-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1402A | NEW | 1520-PDI-1402A | PRESSURE GAUGE - D/P | 1520-PR-PID-0000-EXP-5114 | FIN FAN SIDE STREAM FLT | ------ | 1520-FL-005 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1402 | NEW | 1520-PDIT-1402 | PRESSURE TRANSMITTER - D/P | 1520-PR-PID-0000-EXP-5114 | FIN FAN SIDE STREAM FLT | ------ | 1520-FL-005 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-P-1402 | NEW | 1520-PDI-1402 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | FIN FAN SIDE STREAM FLT | ------ | 1520-FL-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1402 | NEW | 1520-PDAH-1402 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | FIN FAN SIDE STREAM FLT | ------ | 1520-FL-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1403 | NEW | 1520-RO-1403 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5114 | FIN FAN SIDE STREAM FILER INLET AND OUTLET | 6"-CLW-1520-9463-CBA-FP- | 1520-FL-005 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1409 | NEW | 1520-HS-1409 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP | ------ | 1520-PP-009 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-1411 | NEW | 1520-HS-1411 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP (STDBY) | ------ | 1520-PP-010 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-1419 | NEW | 1520-HS-1419 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP | ------ | 1520-PP-008 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TE-1426 | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP | ------ | 1520-PP-010 | Vendor | DCS | AI-W | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-1426 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP | ------ | 1520-PP-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-1426 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP | ------ | 1520-PP-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TAH-1426 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP | ------ | 1520-PP-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TE-1421 | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP | ------ | 1520-PP-008 | Vendor | DCS | AI-W | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-1421 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP | ------ | 1520-PP-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-1421 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP | ------ | 1520-PP-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TAH-1421 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP | ------ | 1520-PP-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TE-1423 | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP | ------ | 1520-PP-009 | Vendor | DCS | AI-W | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-1423 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP | ------ | 1520-PP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TI-1423 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP | ------ | 1520-PP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-8421 | NEW | 1520-TAH-1423 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP | ------ | 1520-PP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1420 | NEW | 1520-VS-1420 | VENDOR SUPPLY VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP |  | 1520-PP-008 | Vendor | DCS | AI-W | DCS | N/A | FLD-EQUIP | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-V-1420 | NEW | 1520-VAH-1420 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP |  | 1520-PP-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1422 | NEW | 1520-VS-1422 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP |  | 1520-PP-009 | Vendor | DCS | AI-W | DCS | N/A | FLD-EQUIP | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-V-1422 | NEW | 1520-VAH-1422 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP |  | 1520-PP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1422 | NEW | 1520-VAHH-1422 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP |  | 1520-PP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1422 | NEW | 1520-VAH-1422 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-009 FIN FAN CW PUMP |  | 1520-PP-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1425 | NEW | 1520-VS-1425 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP |  | 1520-PP-010 | Vendor | AI-W | N/A | DCS | N/A | FLD-EQUIP | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1425 | NEW | 1520-VAHH-1425 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP |  | 1520-PP-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1425 | NEW | 1520-VAH-1425 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP |  | 1520-PP-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1425 | NEW | 1520-VAH-1425 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | 1520-PP-010 FIN FAN CW PUMP |  | 1520-PP-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1410 | NEW | 1520-PI-1410 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP DISCH | 18"-CLW-1520-2354-CBA-- | 1520-PP-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1412 | NEW | 1520-PI-1412 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP (STDBY) | 18"-CLW-1520-2355-CBA-- | 1520-PP-010 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1420 | NEW | 1520-VAHH-1420 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP |  | 1520-PP-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-V-1420 | NEW | 1520-VAH-1420 | VENDOR INTERFACE | 1520-PR-PID-0000-EXP-5114 | 1520-PP-008 FIN FAN CW PUMP |  | 1520-PP-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1420 | NEW | 1520-PI-1420 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP | 1"-CLW-1520-1405-CBA-FP-ET | 1520-PP-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-F-1413 | NEW | 1520-FE-1413 | FLOW ELEMENT - ORIFICE PLATE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW SUPPLY HEADER | 24"-CLW-1520-2356-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-1413 | NEW | 1520-FIT-1413 | FLOW TRANSMITTER - D/P | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-F-1413 | NEW | 1520-FI-1413 | DCS INDICATION | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-1413 | NEW | 1520-FSL-1413 | INTLK | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-1413 | NEW | 1520-FAL-1413 | DCS ALARM | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-F-1413 | NEW | 1520-FSLL-1413 | INTLK | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1410 | NEW | 1520-RO-1410 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP | 1"-CLW-1520-1405-CBA-FP-ET | NA | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1412 | NEW | 1520-RO-1412 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5114 | FIN FAN CW PUMP | 1"-CLW-1520-2354-CBA-FP-ET | NA | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1600 | NEW | 1520-HS-1600 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1600 | NEW | 1520-VSH-1600 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1600 | NEW | 1520-VAH-1600 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1601 | NEW | 1520-HS-1601 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1601 | NEW | 1520-VSH-1601 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1601 | NEW | 1520-VAH-1601 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1602 | NEW | 1520-HS-1602 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1602 | NEW | 1520-VSH-1602 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1602 | NEW | 1520-VAH-1602 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1603 | NEW | 1520-HS-1603 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1603 | NEW | 1520-VSH-1603 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1603 | NEW | 1520-VAH-1603 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1604 | NEW | 1520-HS-1604 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1604 | NEW | 1520-VSH-1604 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1604 | NEW | 1520-VAH-1604 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1605 | NEW | 1520-HS-1605 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1605 | NEW | 1520-VSH-1605 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1605 | NEW | 1520-VAH-1605 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1606 | NEW | 1520-HS-1606 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1606 | NEW | 1520-VSH-1606 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1606 | NEW | 1520-VAH-1606 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1608 | NEW | 1520-HS-1608 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1608 | NEW | 1520-VSH-1608 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1608 | NEW | 1520-VAH-1608 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1609 | NEW | 1520-HS-1609 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1609 | NEW | 1520-VSH-1609 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1609 | NEW | 1520-VAH-1609 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1610 | NEW | 1520-HS-1610 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1610 | NEW | 1520-VSH-1610 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1610 | NEW | 1520-VAH-1610 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1611 | NEW | 1520-HS-1611 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1611 | NEW | 1520-VSH-1611 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1611 | NEW | 1520-VAH-1611 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1612 | NEW | 1520-HS-1612 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1612 | NEW | 1520-VSH-1612 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1612 | NEW | 1520-VAH-1612 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1613 | NEW | 1520-HS-1613 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1613 | NEW | 1520-VSH-1613 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1613 | NEW | 1520-VAH-1613 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1614 | NEW | 1520-HS-1614 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1614 | NEW | 1520-VSH-1614 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1614 | NEW | 1520-VAH-1614 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1616 | NEW | 1520-HS-1616 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1616 | NEW | 1520-VSH-1616 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1616 | NEW | 1520-VAH-1616 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-008 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1617 | NEW | 1520-HS-1617 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1617 | NEW | 1520-VSH-1617 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1617 | NEW | 1520-VAH-1617 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-009 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1618 | NEW | 1520-HS-1618 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1618 | NEW | 1520-VSH-1618 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1618 | NEW | 1520-VAH-1618 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-010 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1619 | NEW | 1520-HS-1619 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1619 | NEW | 1520-VSH-1619 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1619 | NEW | 1520-VAH-1619 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-011 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1620 | NEW | 1520-HS-1620 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1620 | NEW | 1520-VSH-1620 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1620 | NEW | 1520-VAH-1620 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-012 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1621 | NEW | 1520-HS-1621 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1621 | NEW | 1520-VSH-1621 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1621 | NEW | 1520-VAH-1621 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-013 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-1622 | NEW | 1520-HS-1622 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-V-1622 | NEW | 1520-VSH-1622 | VIBRATION SWITCH | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | Vendor | DCS | DI | RIO | 24V | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-V-1622 | NEW | 1520-VAH-1622 | DCS ALARM | 1520-PR-PID-0000-EXP-5116 | FIN FAN COOLERS MOTOR | ------ | 1520-CO-014 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1630 | NEW | 1520-RO-1630 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-2362-CBA-- | 1520-CO-008 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1632 | NEW | 1520-RO-1632 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-2363-CBA-- | 1520-CO-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1634 | NEW | 1520-RO-1634 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-2364-CBA-- | 1520-CO-010 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1636 | NEW | 1520-RO-1636 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-1600-CBA-- | 1520-CO-011 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1638 | NEW | 1520-RO-1638 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-1601-CBA-- | 1520-CO-012 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1640 | NEW | 1520-RO-1640 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-1603-CBA-- | 1520-CO-013 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1642 | NEW | 1520-RO-1642 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-1604-CBA-- | 1520-CO-014 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-R-1644 | NEW | 1520-RO-1644 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5116 | CW RETURN FROM HEADER | 10"-CLW-1520-1604-CBA-- | 1520-CO-014 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1802 | NEW | 1520-TW-1802 | THERMOWELL | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | 24"-CLW-1520-2356-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1802 | NEW | 1520-TE-1802 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | 24"-CLW-1520-2356-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1802 | NEW | 1520-TIT-1802 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-1802 | NEW | 1520-TI-1802 | DCS INDICATION | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1802 | NEW | 1520-TAH-1802 | DCS ALARM | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1812 | NEW | 1520-PI-1812 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | 24"-CLW-1520-2356-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1803 | NEW | 1520-AE-1803 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | 24"-CLW-1520-2356-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1803 | NEW | 1520-AIT-1803 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-1803 | NEW | 1520-AI-1803 | DCS INDICATION | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1803 | NEW | 1520-AAH-1803 | DCS ALARM | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1806 | NEW | 1520-AE-1806 | ANALYZER SENSOR - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | 24"-CLW-1520-2369-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1806 | NEW | 1520-AIT-1806 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-A-1806 | NEW | 1520-AI-1806 | DCS INDICATION | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1806 | NEW | 1520-ADI-1806 | DCS INDICATION | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1806 | NEW | 1520-ADAH-1806 | DCS ALARM | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-1806 | NEW | 1520-AAH-1806 | DCS ALARM | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1807 | NEW | 1520-TW-1807 | THERMOWELL | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | 24"-CLW-1520-2369-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1807 | NEW | 1520-TE-1807 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | 24"-CLW-1520-2369-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1807 | NEW | 1520-TIT-1807 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-T-1807 | NEW | 1520-TI-1807 | DCS INDICATION | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-1807 | NEW | 1520-TAH-1807 | DCS ALARM | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-P-1813 | NEW | 1520-PI-1813 | PRESSURE GAUGE | 1520-PR-PID-0000-EXP-5118 | FIN FAN CW RETURN HEADER | 24"-CLW-1520-2369-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4607 | NEW | 1520-LI-4607 | DCS INDICATION | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4607 | NEW | 1520-LIT-4607 | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-4607 | NEW | 1520-LAH-4607 | DCS ALARM | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4601 | NEW | 1520-AE-4601 | ANALYZER SENSOR - PH | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4601 | NEW | 1520-AIT-4601 | ANALYZER TRANSMITTER - PH | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-4601 | NEW | 1520-AI-4601 | DCS INDICATION | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4602 | NEW | 1520-AE-4602 | ANALYZER SENSOR - PH | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | N/A | E-T | N/A | mV | FLD-EQUIP | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4602 | NEW | 1520-AIT-4602 | ANALYZER TRANSMITTER - PH | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-4602 | NEW | 1520-AI-4602 | DCS INDICATION | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4608 | NEW | 1520-LI-4608 | DCS INDICATION | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4608 | NEW | 1520-LIT-4608 | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-L-4608 | NEW | 1520-LAH-4608 | DCS ALARM | 1520-PR-PID-0000-EXP-5146 | EFFLUENT NEUTRALIZATION PIT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-4701 | NEW | 1520-TE-4701 | TEMPERATURE ELEMENT - TC TYPE K | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-4701 | NEW | 1520-TW-4701 | THERMOWELL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-4701 | NEW | 1520-TIT-4701 | TEMPERATURE INDICATING TRANSMITTER | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-T-4701 | NEW | 1520-TIA-4701 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-4701 | NEW | 1520-TAH-4701 | DCS ALARM | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-T-4701 | NEW | 1520-TAL-4701 | DCS ALARM | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-4702 | NEW | 1520-JI-4702 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | TRANSLOADING EFFLUENT UNLOADING PUMP | ------ | 1520-PP-021 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-4702 | NEW | 1520-HS-4702 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5147 | TRANSLOADING EFFLUENT UNLOADING PUMP | ------ | 1520-PP-021 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-4704 | NEW | 1520-HS-4704 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK AGITATOR | ------ | 1520-AG-003 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LIC-4705 | DCS INDICATION AND CONTROL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LIT-4705 | LEVEL TRANSMITTER - RADAR | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LY-4705 | SMART VALVE POSITIONER | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1520 | N | 1520-JBP-002 | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LCV-4705 | CONTROL VALVE | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | 2"-ACW-1520-0302-SBO-FP-ET | 1520-TK-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LAH-4705 | DCS ALARM | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LSHH-4705 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LSL-4705 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LSH-4705 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK |  | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-L-4705 | NEW | 1520-LSLL-4705 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-4706 | NEW | 1520-JI-4706 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP | ------ | 1520-PP-023 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-4706 | NEW | 1520-HS-4706 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP | ------ | 1520-PP-023 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-4706 | NEW | 1520-JI-4707 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP | ------ | 1520-PP-024 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-H-4707 | NEW | 1520-HS-4707 | MOTOR CONTROL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP | ------ | 1520-PP-024 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1520 | N | SWRK | NO
1500 | 1520 | STRONG ACID | 1520-P-4708 | NEW | 1520-PI-4708 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP DISCH | 2"-ACW-1520-0302-SBO-FP-ET | 1520-PP-023 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-P-4709 | NEW | 1520-PI-4709 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP DISCH | 2"-ACW-1520-0304-SBO-FP-ET | 1520-PP-024 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-P-4710 | NEW | 1520-PI-4710 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT UNLOADING PUMP | 4"-ACW-1520-321-PBB-FP-ET | 1520-PP-024 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-R-4712 | NEW | 1520-RO-4712 | RESTRICTION ORIFICE | 1520-PR-PID-0000-EXP-5147 | EFFLUENT FEED PUMP RECYCLE | 2"-ACW-1520-305-SBO-FP-ET | 1520-PP-023/024 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-AE-4711 | ANALYZER SENSOR - PH | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | 2"-ACW-1520-4708-SBO-FP-ET | 1520-TK-007 | EXP | N/A | E-T | N/A | MV | FLD-INLINE | 1520 | N | N/A | YES
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-AIT-4711 | ANALYZER TRANSMITTER - PH | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1520 | N | 1520-JBP-001 | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-AI-4711 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-ASLL-4711 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-AAH-4711 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-AAL-4711 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-ASL-4711 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TK-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-A-4711 | NEW | 1520-AEV-4711 | SOLENOID VALVE | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | 1-1/2"-CAS-1520-3135-CBN-FP-ET | 1520-TK-007 | EXP | DCS | DO | RIO | 24V | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-XEV-4711 | PART OF VALVE SOLENOID VALVE | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TW-003 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-XV-4711 | ON/OFF VALVE | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | 1-1/2"-CAS-1520-3135-CBN-FP-ET | 1520-TW-003 | EXP | DCS | DCS | DCS | N/A | FLD-INLINE | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-HS-4711 | OPERATOR INITIATED DCS CONTROL | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TW-003 | EXP | DCS | DCS | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-ZSC-4711 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-ZAC-4711 | INTLK | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-ZSO-4711 | PART OF VALVE LIMIT SWITCH | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1520 | N | 1520-JBP-003 | NO
1500 | 1520 | STRONG ACID | 1520-X-4711 | NEW | 1520-ZAO-4711 | DCS INDICATION | 1520-PR-PID-0000-EXP-5147 | EFFLUENT STOR TK | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1520 | N | N/A | NO
1500 | 1520 | STRONG ACID | 1520-H-9010B | NEW | 1520-HS-9010B | PUSHBUTTON | 1520-PR-PID-0000-EXP-5147 | TRANSLOADING EFFLUENT UNLOADING PUMP PUSHBUTTON | ------ | 1520-PP-021 | EXP | N/A | DO | N/A | 24VDC | FLD | 1520 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FE-0003 | FLOW ELEMENT - MAGNETIC | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 30"-ACW-1530-3112-SBO-- | 1530-SR-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FIT-0003 | FLOW TRANSMITTER - MAGNETIC | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | 120 VAC/60 Hz | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FI-0003 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FAL-0003 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FALL-0003 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FAH-0003 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0003 | NEW | 1530-FSLL-0003 | INTLK | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PIT-0004 | PRESSURE TRANSMITTER - DIAPHRAGM SEAL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 30"-ACW-1530-3112-SBO-- | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PIC-0004 | DCS INDICATION AND CONTROL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PAL-0004 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PALL-0004 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PAH-0004 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PSLL-0004 | INTLK | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PY-0004 | SMART VALVE POSITIONER | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0004 | NEW | 1530-PCV-0004 | CONTROL VALVE | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 30"-ACW-1530-3112-SBO-- | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0005 | NEW | 1530-PI-0005 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 30"-ACW-1530-3112-SBO-- | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AE-0002A | ANALYZER SENSOR - PH | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 2"-ACW-1530-3100-SBO-FP-ET | 1530-SR-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AIT-0002A | ANALYZER TRANSMITTER - PH | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AI-0002A | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-TI-0002A | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-ADI-0002 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-ADAH-0002 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AE-0002B | ANALYZER SENSOR - PH | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 2"-ACW-1530-3101-SBO-FP-ET | 1530-SR-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AIT-0002B | ANALYZER TRANSMITTER - PH | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AI-0002B | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-TI-0002B | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AHS-0002 | DCS OPERATOR INITIATED CONTROL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AAH-0002 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AAL-0002 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AIC-0002 | DCS INDICATION AND CONTROL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-AY-0002 | SMART VALVE POSITIONER | 1530-PR-PID-0000-EXP-5100 | CAUSTIC FEED TO TAIL GAS SCRUBBER | ------ | 1530-SR-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0002 | NEW | 1530-ACV-0002 | CONTROL VALVE | 1530-PR-PID-0000-EXP-5100 | CAUSTIC FEED TO TAIL GAS SCRUBBER | 2"-CAS-1510-0108-CBN-FP-ET | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-D-0006 | NEW | 1530-DE-0006 | CORIOLIS FLOW ELEMENT | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 2"-ACW-1530-3100-SBO-FP-ET | 1530-SR-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-D-0006 | NEW | 1530-DIT-0006 | CORIOLIS FLOW TRANSMITTER | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-D-0006 | NEW | 1530-DIC-0006 | DCS INDICATION AND CONTROL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-D-0006 | NEW | 1530-DAH-0006 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-D-0006 | NEW | 1530-DY-0006 | SMART VALVE POSITIONER | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | ------ | 1530-SR-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-D-0006 | NEW | 1530-DCV-0006 | CONTROL VALVE | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 3"-ACW-1520-3104-SBO-FP-ET | 1530-SR-001 | 5015 | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LG-0014 | LEVEL GAUGE - MAGNETIC | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LIT-0014A | MAGNETOSTRICTIVE LIT | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LIT-0014B | MAGNETOSTRICTIVE LIT | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LI-0014 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LI-0014A | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LI-0014B | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LALL-0014 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LAL-0014 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LAH-0014 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LAHH-0014 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LSHH-0014 | INTLK | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0014 | NEW | 1530-LSLL-0014 | INTLK | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL |  | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-H-0013 | NEW | 1530-HS-0013 | DCS OPERATOR INITIATED CONTROL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LIT-0013 | LEVEL TRANSMITTER - GWR | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LIC-0013 | DCS INDICATION AND CONTROL | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LI-0013 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LALL-0013 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LAL-0013 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LAH-0013 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LAHH-0013 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LSLL-0013 | INTLK | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LSHH-0013 | INTLK | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LY-0013 | SMART VALVE POSITIONER | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | ------ | 1530-SR-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-L-0013 | NEW | 1530-LCV-0013 | CONTROL VALVE | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER LEVEL | 4"-RAW-1530-5122-CBA-FP-ET | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-R-0017 | NEW | 1530-RO-0017 | RESTRICTION ORIFICE | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 2"-ACW-1530-3101-SBO-FP-ET | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-R-0007 | NEW | 1530-RO-0007 | RESTRICTION ORIFICE | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER WEAK ACID INLET | 2"-ACW-1530-3100-SBO-FP-ET | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0008 | NEW | 1530-PDIT-0008 | PRESSURE TRANSMITTER - D/P | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER CHEVRON | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0008 | NEW | 1530-PDI-0008 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER CHEVRON | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0008 | NEW | 1530-PDAH-0008 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER CHEVRON | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0008 | NEW | 1530-FI-0008A | FLOW GAUGE - ROTAMETER | 1530-PR-PID-0000-EXP-5100 | PURGE FOR PDIT-0008 | ------ | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0008 | NEW | 1530-FI-0008B | FLOW GAUGE - ROTAMETER | 1530-PR-PID-0000-EXP-5100 | PURGE FOR PDIT-0008 | ------ | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0009 | NEW | 1530-PDIT-0009 | PRESSURE TRANSMITTER - D/P | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER MESH PAD | ------ | 1530-SR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0009 | NEW | 1530-PDI-0009 | DCS INDICATION | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER MESH PAD | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0009 | NEW | 1530-PDAH-0009 | DCS ALARM | 1530-PR-PID-0000-EXP-5100 | TAIL GAS SCRUBBER MESH PAD | ------ | 1530-SR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0009A | NEW | 1530-FI-0009A | FLOW GAUGE - ROTAMETER | 1530-PR-PID-0000-EXP-5100 | PURGE FOR PDIT-0009 | ------ | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0009B | NEW | 1530-FI-0009B | FLOW GAUGE - ROTAMETER | 1530-PR-PID-0000-EXP-5100 | PURGE FOR PDIT-0009 | ------ | 1530-SR-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-R-0201 | NEW | 1530-RO-0201 | RESTRICTION ORIFICE | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | 1"-ACW-1530-0402-SBO-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0210 | NEW | 1530-PI-0210 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | 36"-ACW-1530-3103-SBO-- | 1530-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0211 | NEW | 1530-PI-0211 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | 36"-ACW-1530-0002-SBO-- | 1530-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0212 | NEW | 1530-PI-0212 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | 30"-ACW-1530-3112-SBO-- | 1530-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0213 | NEW | 1530-PI-0213 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | 30"-ACW-1530-3113-SBO-- | 1530-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-V-0220 | NEW | 1530-VS-0220 | VENDOR SUPPLY VIBRATION SWITCH | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | Vendor | DCS | AI-W | DCS | N/A | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-V-0220 | NEW | 1530-VAH-0220 | VENDOR INTERFACE | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-V-0220 | NEW | 1530-VAH-0220 | DCS ALARM | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0221 | NEW | 1530-TE-0221 | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | Vendor | DCS | AI-W | DCS | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0221 | NEW | 1530-TI-0221 | DCS INDICATION | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-V-0225 | NEW | 1530-VS-0225 | VENDOR SUPPLY VIBRATION SWITCH | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | Vendor | DCS | AI-W | DCS | N/A | FLD-EQUIP | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-V-0225 | NEW | 1530-VAH-0225 | VENDOR INTERFACE | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-V-0225 | NEW | 1530-VAH-0225 | DCS ALARM | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0226 | NEW | 1530-TE-0226 | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | Vendor | DCS | AI-W | DCS | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0226 | NEW | 1530-TI-0226 | VENDOR INTERFACE | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0226 | NEW | 1530-TI-0226 | DCS INDICATION | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0226 | NEW | 1530-TAH-0226 | DCS ALARM | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0221 | NEW | 1530-TI-0221 | VENDOR INTERFACE | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0221 | NEW | 1530-TAH-0221 | DCS ALARM | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP | ------ | 1530-PP-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0241 | NEW | 1530-AE-0241 | SO2 AREA MONITOR SENSOR | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER | ------ | N/A | EXP | N/A | E-T | N/A | mV | FLD-OFFLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0241 | NEW | 1530-AIT-0241 | SO2 AREA MONITOR | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0241 | NEW | 1530-AI-0241 | DCS INDICATION | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0241 | NEW | 1530-AAH-0241 | DCS ALARM | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0241 | NEW | 1530-AAHH-0241 | DCS ALARM | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0241 | NEW | 1530-ASH-0241 | INTLK | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0241 | NEW | 1530-XA-0241A | ALARM BEACON | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER PUMP | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0241 | NEW | 1530-XA-0241B | ALARM HORN | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER PUMP | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-H-0290 | NEW | 1530-HS-0290A | MOTOR CONTROL | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP STOP | ------ | 1530-PP-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1530 | N | SWRK | NO
1500 | 1530 | GAS TREATMENT | 1530-H-0290 | NEW | 1530-HS-0290B | MOTOR CONTROL | 1530-PR-PID-0000-EXP-5102 | TAIL GAS SCRUBBER CIRCULATION PUMP STOP | ------ | 1530-PP-002 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1530 | N | SWRK | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0420 | NEW | 1530-TW-0420 | THERMOWELL | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | 72"-SOX-1530-3109-D2205-- | 1530-ST-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0420 | NEW | 1530-TE-0420 | TEMPERATURE ELEMENT - TC TYPE K | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | 72"-SOX-1530-3109-D2205-- | 1530-ST-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0420 | NEW | 1530-TIT-0420 | TEMPERATURE INDICATING TRANSMITTER | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0420 | NEW | 1530-TI-0420 | DCS INDICATION | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0420 | NEW | 1530-TAH-0420 | DCS ALARM | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0465 | NEW | 1530-AE-0465 | CEMS-ANALYZER PROBE | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0465 | NEW | 1530-AIT-0465 | CEMS-ANALYZER | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | Non-UPS, 208Y/120VAC 3 PH 25 A (might go up to 30A once all components and sample line lengths are comfirmed) | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0465 | NEW | 1530-AI-0465 | DCS INDICATION | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0465 | NEW | 1530-AAH-0465 | DCS ALARM | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0460 | NEW | 1530-AIT-0460 | CEMS-ANALYZER | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | UPS , 208Y/120VAC 3 PH 25 A (might go up to 30A once all components and sample line lengths are comfirmed) | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0460 | NEW | 1530-AI-0460 | DCS INDICATION | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0460 | NEW | 1530-AAH-0460 | DCS ALARM | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0461 | NEW | 1530-AIT-0461 | CEMS-ANALYZER | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0461 | NEW | 1530-AI-0461 | DCS INDICATION | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-A-0461 | NEW | 1530-AAL-0461 | DCS ALARM | 1530-PR-PID-0000-EXP-5104 | PGS FROM TAIL GAS SCUBBER TO STACK | ------ | 1530-ST-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-H-0657 | NEW | 1530-HS-0657 | MOTOR CONTROL | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWER | ------ | 1530-GB-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1530 | N | SWRK | NO
1500 | 1530 | GAS TREATMENT | 1530-H-0667 | NEW | 1530-HS-0667 | MOTOR CONTROL | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWER | ------ | 1530-GB-002 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1530 | N | SWRK | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0651 | NEW | 1530-PI-0651 | VENDOR SUPPLY PRESSURE GAUGE | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWER | 6"-SOX-1530-3122-CBP-PP- | 1530-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0661 | NEW | 1530-PI-0661 | VENDOR SUPPLY PRESSURE GAUGE | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWER | 6"-SOX-1530-3123-CBP-PP- | 1530-GB-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0658 | NEW | 1530-PSV-0658 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWER OUTLET | 6"-SOX-1530-3122-CBP-PP- | 1530-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0668 | NEW | 1530-PSV-0668 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWER OUTLET | 6"-SOX-1530-3123-CBP-PP- | 1530-GB-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0653 | NEW | 1530-TW-0653 | THERMOWELL | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | 6"-SOX-1530-3122-CBP-PP- | 1530-GB-001/002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0653 | NEW | 1530-TE-0653 | TEMPERATURE ELEMENT - TC TYPE K | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | 6"-SOX-1530-3122-CBP-PP- | 1530-GB-001/002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0653 | NEW | 1530-TIT-0653 | TEMPERATURE INDICATING TRANSMITTER | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0653 | NEW | 1530-TI-0653 | DCS INDICATION | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0653 | NEW | 1530-TAH-0653 | DCS ALARM | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0652 | NEW | 1530-PIT-0652 | PRESSURE TRANSMITTER | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | 6"-SOX-1530-3122-CBP-PP- | 1530-GB-001/002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0652 | NEW | 1530-PIA-0652 | DCS INDICATION | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0652 | NEW | 1530-PAH-0652 | DCS ALARM | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0652 | NEW | 1530-PAHH-0652 | DCS ALARM | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0652 | NEW | 1530-PSHH-0652 | INTLK | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR BLOWERS DISCH | ------ | 1530-GB-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-P-0671 | NEW | 1530-PI-0671 | PRESSURE GAUGE | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | 1"-RAW-1530-3108-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TW-0654 | THERMOWELL | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | 6"-SOX-1530-3124-SBO-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TE-0654 | TEMPERATURE ELEMENT - TC TYPE K | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | 6"-SOX-1530-3124-SBO-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TIT-0654 | TEMPERATURE INDICATING TRANSMITTER | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TIA-0654 | DCS INDICATION | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TAH-0654 | DCS ALARM | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TAHH-0654 | DCS ALARM | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-T-0654 | NEW | 1530-TSHH-0654 | INTLK | 1530-PR-PID-0000-EXP-5106 | OXIDATION AIR TO TAIL GAS SCRUBBER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-XEV-0656 | PART OF VALVE SOLENOID VALVE | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-XV-0656 | ON/OFF VALVE | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | 1"-RAW-1530-3108-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | YES
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-ZSC-0656 | PART OF VALVE LIMIT SWITCH | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | ------ | N/A | EXP | DCS | DI | RIO | 24V | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-ZAC-0656 | DCS INDICATION | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-ZSO-0656 | PART OF VALVE LIMIT SWITCH | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | ------ | N/A | EXP | DCS | DI | RIO | 24V | FLD-INT | 1530 | N | 1530-JBP-001 | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-ZAO-0656 | DCS INDICATION | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-X-0656 | NEW | 1530-HS-0656 | DCS OPERATOR INITIATED CONTROL | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1530 | N | N/A | NO
1500 | 1530 | GAS TREATMENT | 1530-F-0659 | NEW | 1530-FI-0659 | FLOW GAUGE - ROTAMETER | 1530-PR-PID-0000-EXP-5106 | RAW WATER SUPPLY TO HUMIDIFICATION NOZZLE | 1"-RAW-1530-3108-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1530 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PI-6801 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5068 | 1540-PV-002 DEAERATOR |  | 1540-PV-002 | Vendor | NA | NA | NA | NA | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6810 | NEW | 1540-PI-6810 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5068 | CW TO BFW SAMPLE COOLER | 1"-CLW-1540-6714-CBA-FP-ET | 1540CO-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-6811 | NEW | 1540-PI-6811 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5068 | CW RETURN FROM BFW SAMPLE COOLER | 1"-CLW-1540-4117-CBA-FP-ET | 1540-CO-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-6880 | NEW | 1540-PSV-6880 | PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5068 | BFW SAMPLE COOLER CW RETURN | 1"-CLW-1540-4117-CBA-FP-ET | 1540-CO-009 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-R-6882 | NEW | 1540-RO-6882 | VENDOR SUPPLY ORIFICE PLATE | 1540-PR-PID-0000-EXP-5068 | BFW TO DEAERATOR | 3"-BFW-1520-9225-CEA-HC- | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6842 | NEW | 1540-LSLL-6842 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL LOW-LOW | ------ | 1540-PV-002 | Vendor | DCS | DI-S | DCS | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6842 | NEW | 1540-LALL-6842 | INTLK | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL LOW-LOW | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6841 | NEW | 1540-LSHH-6841 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1540-PR-PID-0000-EXP-5068 | DEAERATORE STOR LEVEL HIGH-HIGH | ------ | 1540-PV-002 | Vendor | DCS | DI-S | DCS | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6841 | NEW | 1540-LAHH-6841 | INTLK | 1540-PR-PID-0000-EXP-5068 | DEAERATORE STOR LEVEL HIGH-HIGH | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6843 | NEW | 1540-LEV-6843 | PART OF VALVE SOLENOID VALVE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR OVERFLOW | 8"-BFW-1540-9216-CBO-PP- | 1540-PV-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6843 | NEW | 1540-LV-6843 | ON/OFF VALVE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR OVERFLOW | 8"-BFW-1540-9216-CBO-PP- | 1540-PV-002 | Vendor | DCS | DCS | DCS | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-6843 | NEW | 1540-XEV-6843 | PART OF VALVE SOLENOID VALVE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR OVERFLOW | 8"-BFW-1540-9216-CBO-PP- | 1540-PV-002 | Vendor | DCS | DO | RIO | 24V | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-6843 | NEW | 1540-XV-6843 | VENDOR SUPPLY ON/OFF VALVE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR OVERFLOW | 8"-BFW-1540-9216-CBO-PP- | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6850 | NEW | 1540-LG-6850 | VENDOR SUPPLY LEVEL GAUGE - SIGHT GLASS | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6821 | NEW | 1540-TW-6821 | VENDOR SUPPLY THERMOWELL | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR TEMP | ------ | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6821 | NEW | 1540-TE-6821 | VENDOR SUPPLY TEMPERATURE ELEMENT | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR TEMP | ------ | 1540-PV-002 | Vendor | N/A | E-T | N/A | mV | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6821 | NEW | 1540-TT-6821 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR TEMP | ------ | 1540-PV-002 | Vendor | DCS | AI-HART-S | PLC | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6821 | NEW | 1540-TI-6821 | DCS INDICATION | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR TEMP | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6821 | NEW | 1540-TAH-6821 | DCS ALARM | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR TEMP | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6840 | NEW | 1540-LIT-6840 | VENDOR SUPPLY LEVEL TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | Vendor | DCS | AI-HART | PLC | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6840 | NEW | 1540-LIC-6840 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | EXP | DCS | AI-HART-S | DCS | 4-20mA HART | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6840 | NEW | 1540-LAL-6840 | DCS ALARM | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6840 | NEW | 1540-LAH-6840 | DCS ALARM | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PIT-6801 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | ------ | 1540-PV-002 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PIC-6801 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PAH-6801 | DCS ALARM | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PAL-6801 | DCS ALARM | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PY-6801 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | ------ | 1540-PV-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6801 | NEW | 1540-PCV-6801 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | 8"-LPS-1540-4200-CBO-HC- | 1540-PV-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6881 | NEW | 1540-PSV-6881 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR | 8"-LPS-1540-8618-CBO-HC- | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6820 | NEW | 1540-TW-6820 | THERMOWELL | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR TEMP | ------ | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6820 | NEW | 1540-TE-6820 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR TEMP | ------ | 1540-PV-002 | Vendor | N/A | E-T | N/A | mV | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6820 | NEW | 1540-TIT-6820 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR TEMP | ------ | 1540-PV-002 | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6820 | NEW | 1540-TI-6820 | DCS INDICATION | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR TEMP | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-6820 | NEW | 1540-TAH-6820 | DCS ALARM | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR TEMP | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-6821 | NEW | 1540-PI-6821 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5068 | DEAERATOR SEPARATOR PRESS | ------ | 1540-PV-002 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7012 | NEW | 1540-PI-7012 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1540-PR-PID-0000-EXP-5070 | CHEMICAL DOSING FOR BFW | 1"-CHD-1540-4145-SDA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-7000 | NEW | 1540-PIT-7000 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5070 | BFW PUMPS PRESS | 8"-BFW-1540-4125-CEA-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7000 | NEW | 1540-PIA-7000 | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | BFW PUMPS PRESS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7000 | NEW | 1540-PAL-7000 | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | BFW PUMPS PRESS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7000 | NEW | 1540-PSL-7000 | INTLK | 1540-PR-PID-0000-EXP-5070 | BFW PUMPS PRESS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7000 | NEW | 1540-PSLL-7000 | INTLK | 1540-PR-PID-0000-EXP-5070 | BFW PUMPS PRESS | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7070 | NEW | 1540-FE-7070 | FLOW ELEMENT - VORTEX | 1540-PR-PID-0000-EXP-5070 | BFW SUPPLY FLOW | 8"-BFW-1540-4125-CEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7070 | NEW | 1540-FIT-7070 | FLOW TRANSMITTER - VORTEX | 1540-PR-PID-0000-EXP-5070 | BFW SUPPLY FLOW | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7070 | NEW | 1540-FIC-7070 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5070 | BFW SUPPLY FLOW | ------ | N/A | EXP | DCS | AI-HART-S | DCS | 4-20mA HART | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7070 | NEW | 1540-FY-7070 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5070 | BFW SUPPLY FLOW | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7070A | NEW | 1540-FY-7070A | DCS CONTROL FUNCTION | 1540-PR-PID-0000-EXP-5070 | BFW SUPPLY FLOW | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7070 | NEW | 1540-FCV-7070 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5070 | BFW SUPPLY FLOW | 8"-BFW-1540-9223-CEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-R-7009 | NEW | 1540-RO-7009 | RESTRICTION ORIFICE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMPS DISCH | 1"-BFW-1540-4126-CEA-HC-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7010 | NEW | 1540-PI-7010 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP INLET | 8"-BFW-1540-4120-CBO-HC- | 1540-PP-017 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7011 | NEW | 1540-PI-7011 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP OUTLET | 8"-BFW-1540-4128-CEA-HC- | 1540-PP-017 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7016 | NEW | 1540-PI-7016 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP INLET | 8"-BFW-1540-4125-CEA-HC- | 1540-PP-018 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7017 | NEW | 1540-PI-7017 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP OUTLET | 8"-BFW-1540-4121-CBO-HC- | 1540-PP-018 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7014 | NEW | 1540-PI-7014 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP COOLER | 1"-CLW-1540-6711-CBA-FP-ET | 1540-PP-017 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-7015 | NEW | 1540-PI-7015 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP COOLER | 1"-CLW-1540-6712-CBA-FP-ET | 1540-PP-018 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-H-7090 | NEW | 1540-HS-7090A | MOTOR CONTROL | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP START/STOP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1540 | N | SWRK | NO
1500 | 1540 | CONTACT SECTION | 1540-H-7090 | NEW | 1540-HS-7090B | MOTOR CONTROL | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP (STANDBY) START/STOP | ------ | 1540-PP-018 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1540 | N | SWRK | NO
1500 | 1540 | CONTACT SECTION | 1540-V-7020 | NEW | 1540-VS-7020 | VENDOR SUPPLY VIBRATION SWITCH | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | NA | N/A | N/A | AI-W | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-7020 | NEW | 1540-VAH-7020 | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-7020 | NEW | 1540-VAH-7020 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021A | NEW | 1540-TE-7021A | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | NA | AI-W | N/A | N/A | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021A | NEW | 1540-TI-7021A | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021A | NEW | 1540-TAH-7021A | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021A | NEW | 1540-TI-7021A | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021B | NEW | 1540-TE-7021B | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | N/A | AI-W | N/A | N/A | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021B | NEW | 1540-TI-7021B | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021B | NEW | 1540-TAH-7021B | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021B | NEW | 1540-TI-7021B | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021C | NEW | 1540-TE-7021C | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | N/A | AI-W | N/A | N/A | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021C | NEW | 1540-TI-7021C | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021C | NEW | 1540-TAH-7021C | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7021C | NEW | 1540-TI-7021C | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026A | NEW | 1540-TE-7026A | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | NA | AI-W | N/A | N/A | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026A | NEW | 1540-TI-7026A | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026A | NEW | 1540-TAH-7026A | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026A | NEW | 1540-TI-7026A | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026B | NEW | 1540-TE-7026B | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | NA | AI-W | N/A | N/A | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026B | NEW | 1540-TI-7026B | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026B | NEW | 1540-TAH-7026B | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026B | NEW | 1540-TI-7026B | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026C | NEW | 1540-TE-7026C | VENDOR SUPPLY TEMPERATURE ELEMENT - RTD PT100 | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | Vendor | NA | AI-W | N/A | N/A | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026C | NEW | 1540-TI-7026C | DCS INDICATION | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026C | NEW | 1540-TAH-7026C | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7026C | NEW | 1540-TI-7026C | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP | ------ | 1540-PP-017 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-7025 | NEW | 1540-VS-7025 | VENDOR SUPPLY VIBRATION SWITCH | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP STANDBY | ------ | 1540-PP-018 | Vendor | NA | N/A | N/A | AI-W | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-7025 | NEW | 1540-VAH-7025 | DCS ALARM | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP STANDBY | ------ | 1540-PP-018 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-7025 | NEW | 1540-VAH-7025 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5070 | HP BFW PUMP STANDBY | ------ | 1540-PP-018 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7225 | NEW | 1540-TW-7225 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | PGS FROM CONV PASS 4 TO HP SH 4A | 78"-SOX-1540-2115-304SS-HC- | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7225 | NEW | 1540-TE-7225 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | PGS FROM CONV PASS 4 TO HP SH 4A | 78"-SOX-1540-2115-304SS-HC- | 1540-HX-004 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7225 | NEW | 1540-TIT-7225 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | PGS FROM CONV PASS 4 TO HP SH 4A | ------ | 1540-HX-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7225 | NEW | 1540-TI-7225 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | PGS FROM CONV PASS 4 TO HP SH 4A | ------ | 1540-HX-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7244 | NEW | 1540-PI-7244 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7246 | NEW | 1540-PI-7246 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | HP STEAM FROM HP SH 4A | ------ | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7250 | NEW | 1540-PI-7250 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | STEAM FROM WHB STEAM DRUM TO HP SH 4A | ------ | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7251 | NEW | 1540-TW-7251 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | STEAM FROM WHB STEAM DRUM TO HP SH 4A | ------ | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7251 | NEW | 1540-TI-7251 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | STEAM FROM WHB STEAM DRUM TO HP SH 4A | ------ | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7252 | NEW | 1540-TW-7252 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7252 | NEW | 1540-TI-7252 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7249 | NEW | 1540-TW-7249 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | HP SH 4A HP STEAM OUTLET | ------ | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7249 | NEW | 1540-TI-7249 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | HP SH 4A HP STEAM OUTLET | ------ | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7247 | NEW | 1540-TW-7247 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | HP STEAM FROM HP SH 4A | 12"-HPS-1540-9434-AEA-HC- | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7228 | NEW | 1540-TE-7228 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | HP SH 4A HP STEAM OUTLET | 12"-HPS-1540-4203-CDB-HC- | 1540-HX-004 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7247 | NEW | 1540-TIT-7247 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | HP STEAM FROM HP SH 4A | ------ | 1540-HX-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7247 | NEW | 1540-TI-7247 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | HP STEAM FROM HP SH 4A | ------ | 1540-HX-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7248 | NEW | 1540-TW-7248 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A HP STEAM OUTLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7248 | NEW | 1540-TI-7248 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A HP STEAM OUTLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7228 | NEW | 1540-TW-7228 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | HP SH 4A HP STEAM OUTLET | 12"-HPS-1540-4203-CDB-HC- | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TE-7221 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | 72"-SOX-1540-4100-304SS-HC- | 1540-HX-007 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7228 | NEW | 1540-TIT-7228 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | HP SH 4A HP STEAM OUTLET | ------ | 1540-HX-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7228 | NEW | 1540-TI-7228 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | HP SH 4A HP STEAM OUTLET | ------ | 1540-HX-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7211 | NEW | 1540-PI-7211 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW INLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-T-7230 | NEW | 1540-TW-7230 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW INLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7230 | NEW | 1540-TI-7230 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW INLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TW-7221 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | 72"-SOX-1540-4100-304SS-HC- | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7223 | NEW | 1540-TE-7223 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | BFW FROM HP SH 4A TO STEAM DRUM | 10"-BFW-1540-4151-CDB-HC- | 1540-PV-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TIT-7221 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | ------ | 1540-HX-007 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TIC-7221 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | ------ | 1540-HX-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TY-7221 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | ------ | 1540-HX-007 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TCV-7221 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | 6"-BFW-1540-4147-CEA-HC- | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TAH-7221 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | ------ | 1540-HX-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7221 | NEW | 1540-TAL-7221 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON 4A PGS OUTLET | ------ | 1540-HX-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7215 | NEW | 1540-PI-7215 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4C BFW INLET | ------ | 1540-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7212 | NEW | 1540-PI-7212 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7231 | NEW | 1540-TW-7231 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | 8"-BFW-1540-4148-CDB-HC- | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7231 | NEW | 1540-TI-7231 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | 8"-BFW-1540-4148-CDB-HC- | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7229 | NEW | 1540-TW-7229 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 3B BFW INLET | ------ | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7229 | NEW | 1540-TI-7229 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 3B BFW INLET | ------ | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7250 | NEW | 1540-PSV-7250 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5072 | HPS FROM HP SH 4A to SH 1B | 12"-HPS-1540-9434-AEA-HC- | N/A | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7223 | NEW | 1540-TW-7223 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | BFW FROM HP SH 4A TO STEAM DRUM | 10"-BFW-1540-4151-CDB-HC- | 1540-PV-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7227 | NEW | 1540-TE-7227 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | BFW FROM ECON 3B TO ECON 4C | 8"-BFW-1540-4149-CEA-HC- | 1540-HX-006 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7223 | NEW | 1540-TIT-7223 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | BFW FROM HP SH 4A TO STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7223 | NEW | 1540-TI-7223 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | BFW FROM HP SH 4A TO STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7223 | NEW | 1540-TAH-7223 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | BFW FROM HP SH 4A TO STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7227 | NEW | 1540-TW-7227 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | BFW FROM ECON 3B TO ECON 4C | 8"-BFW-1540-4149-CEA-HC- | 1540-HX-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7220 | NEW | 1540-TE-7220 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | BFW TO ECON 3B | 8"-BFW-1540-4148-CEA-HC- | 1540-HX-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7227 | NEW | 1540-TIT-7227 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | BFW FROM ECON 3B TO ECON 4C | ------ | 1540-HX-006 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7227 | NEW | 1540-TI-7227 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | BFW FROM ECON 3B TO ECON 4C | ------ | 1540-HX-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7220 | NEW | 1540-TW-7220 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | BFW TO ECON 3B | 8"-BFW-1540-4148-CEA-HC- | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7222 | NEW | 1540-TE-7222 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | PGS FROM CIP HEAT EXCH TO ECON 3B | 78"-SOX-1540-2124-304SS-HC- | 1540-HX-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7220 | NEW | 1540-TIT-7220 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | BFW TO ECON 3B | ------ | 1540-HX-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7220 | NEW | 1540-TI-7220 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | BFW TO ECON 3B | ------ | 1540-HX-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7220 | NEW | 1540-TAL-7220 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | BFW TO ECON 3B | ------ | 1540-HX-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7241 | NEW | 1540-LIT-7241 | LEVEL TRANSMITTER - GWR | 1540-PR-PID-0000-EXP-5072 | ECON 4A DRAIN POT | 4"-ACC-1540-9407-SBQ-FP-ET | 1540-HX-007 | EXP | DCS | AI-HART | DCS | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7241 | NEW | 1540-LI-7241 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | ECON 4A DRAIN POT | ------ | 1540-HX-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7241 | NEW | 1540-LAH-7241 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON 4A DRAIN POT | ------ | 1540-HX-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7240 | NEW | 1540-LIT-7240 | LEVEL TRANSMITTER - GWR | 1540-PR-PID-0000-EXP-5072 | ECON 3B DRAIN POT | 4"-ACC-1540-9418-SBQ-FP-ET | 1540-HX-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7240 | NEW | 1540-LI-7240 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | ECON 3B DRAIN POT | ------ | 1540-HX-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7240 | NEW | 1540-LAH-7240 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON 3B DRAIN POT | ------ | 1540-HX-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7214 | NEW | 1540-PI-7214 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 3B BFW OUTLET | 8"-BFW-1540-4149-CEA-HC- | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7233 | NEW | 1540-TW-7233 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 3B BFW OUTLET | 8"-BFW-1540-4149-CEA-HC- | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7233 | NEW | 1540-TI-7233 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 3B BFW OUTLET | 8"-BFW-1540-4149-CEA-HC- | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7254 | NEW | 1540-TW-7254 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 3B BFW OUTLET | ------ | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7254 | NEW | 1540-TI-7254 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4C BFW OUTLET | ------ | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7213 | NEW | 1540-PI-7213 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4C BFW OUTLET | 8"-BFW-1540-4149-CEA-HC- | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7242 | NEW | 1540-TW-7242 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-005 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7242 | NEW | 1540-TI-7242 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-005 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7243 | NEW | 1540-TW-7243 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7243 | NEW | 1540-TI-7243 | TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5072 | ECON 4A BFW OUTLET | ------ | 1540-HX-007 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7222 | NEW | 1540-TW-7222 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | PGS FROM CIP HEAT EXCH TO ECON 3B | 78"-SOX-1540-2124-304SS-HC- | 1540-HX-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TE-7224 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | 78"-SOX-1540-4101-304SS-HC- | 1520-TW-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7222 | NEW | 1540-TIT-7222 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | PGS FROM CIP HEAT EXCH TO ECON 3B | ------ | 1540-HX-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7222 | NEW | 1540-TI-7222 | DCS INDICATION | 1540-PR-PID-0000-EXP-5072 | PGS FROM CIP HEAT EXCH TO ECON 3B | ------ | 1540-HX-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TW-7224 | THERMOWELL | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | 78"-SOX-1540-4101-304SS-HC- | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7420 | NEW | 1540-TE-7420 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | 10"-HPS-1540-4166-CEA-HC- | 1540-HX-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TIT-7224 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | ------ | 1520-TW-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TAH-7224 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TAL-7224 | DCS ALARM | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TIC-7224 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TY-7224 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | ------ | 1520-TW-003 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7224 | NEW | 1540-TCV-7224 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5072 | ECON 3B BYPASS | 6"-BFW-1540-4150-CEA-HC- | 1520-TW-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TY-7810 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5072 | HP SH 4A BYPASS | ------ | 1540-HX-004 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TCV-7810 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5072 | HP SH 4A BYPASS | 8"-HPS-1540-4207-CEA-HC- | 1540-HX-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7411 | NEW | 1540-PI-7411 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5074 | HP STEAM SAMPLE COOLER CW OUTLET | 1"-CLW-1540-4153-CBA-FP-ET | 1540-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-7481 | NEW | 1540-PSV-7481 | PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5074 | HP STEAM SAMPLE COOLER CW OUTLET | 1"-CLW-1540-4153-CBA-FP-ET | 1540-CO-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-7412 | NEW | 1540-PI-7412 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5074 | HP BOILER BLOWDOWN SAMPLE COOLER CW OUTLET | 1"-CLW-1540-9442-CBA-FP-ET | 1540-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-P-7482 | NEW | 1540-PSV-7482 | PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5074 | HP BOILER BLOWDOWN SAMPLE COOLER CW OUTLET | 1"-CLW-1540-9442-CBA-FP-ET | 1540-CO-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LIT-7440A | VENDOR SUPPLY LEVEL TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LI-7440A | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LAH-7440A | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LAL-7440A | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LALL-7440A | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LSLL-7440A | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-HS-7440 | DCS SELECTOR | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LSHH-7440A | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LIT-7440B | VENDOR SUPPLY LEVEL TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LI-7440B | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LAH-7440B | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LAL-7440B | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LSLL-7440B | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LSHH-7440B | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LSLL-7440 | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LSHH-7440 | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7440 | NEW | 1540-LIC-7440 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LE-7441 | VENDOR SUPPLY EYE-HYE LEVEL ELEMENT | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | DI-S | PLC | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LI-7441 | VENDOR SUPPLY LEVEL INDICATOR | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | DI-S | DCS | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LSHH-7441 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | DI-S | PLC | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LAHH-7441 | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LSH-7441 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | DI-S | PLC | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LAH-7441 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LSL-7441 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | DI-S | PLC | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LAL-7441 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LSLL-7441 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | DCS | DI-S | PLC | 24V | PECS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LALL-7441 | INTLK | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7441 | NEW | 1540-LHA-7441 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7450A | NEW | 1540-LI-7450A | VENDOR SUPPLY LEVEL GAUGE - SIGHT GLASS | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7450B | NEW | 1540-LI-7450B | VENDOR SUPPLY LEVEL GAUGE - SIGHT GLASS | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM LEVEL | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7401 | NEW | 1540-PIT-7401 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM PRESS | ------ | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7401 | NEW | 1540-PI-7401 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM PRESS | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7401 | NEW | 1540-PAH-7401 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM PRESS | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7480A | NEW | 1540-PSV-7480A | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7480C | NEW | 1540-PSV-7480C | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7480B | NEW | 1540-PSV-7480B | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7410 | NEW | 1540-PI-7410 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5074 | WHB STEAM DRUM PRESS | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7400 | NEW | 1540-PIT-7400 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5074 | WHB HP STEAM OUTLET | 10"-HPS-1540-4166-CEA-HC- | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7400 | NEW | 1540-PI-7400 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | WHB HP STEAM OUTLET | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7400 | NEW | 1540-PAL-7400 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB HP STEAM OUTLET | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7400 | NEW | 1540-PAH-7400 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | WHB HP STEAM OUTLET | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7420 | NEW | 1540-TW-7420 | THERMOWELL | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | 10"-HPS-1540-4166-CEA-HC- | 1540-HX-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7421 | NEW | 1540-TE-7421 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5074 | PGS FROM WHB TO JUG VALVE | 78"-SOX-1540-2106-304SS-HC- | 1540-HX-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7420 | NEW | 1540-TIT-7420 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | ------ | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7420 | NEW | 1540-TI-7420 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7470 | NEW | 1540-FE-7470 | FLOW NOZZLE | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | 10"-HPS-1540-4166-CEA-HC- | 1540-HX-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7470 | NEW | 1540-FIT-7470 | FLOW TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | ------ | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7470 | NEW | 1540-FY-7470 | DCS CALCULATION | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7470 | NEW | 1540-FI-7470 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | HP SATURATED STEAM TO SH 4A | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7421 | NEW | 1540-TW-7421 | THERMOWELL | 1540-PR-PID-0000-EXP-5074 | PGS FROM WHB TO JUG VALVE | 78"-SOX-1540-2106-304SS-HC- | 1540-HX-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7821 | NEW | 1540-TE-7821 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5078 | PGS FROM CONV PASS 1 TO HP SH 1B | 84"-SOX-1540-2110-304SS-HC- | 1540-HX-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7421 | NEW | 1540-TIT-7421 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5074 | PGS FROM WHB TO JUG VALVE | ------ | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7421 | NEW | 1540-TI-7421 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | PGS FROM WHB TO JUG VALVE | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7422 | NEW | 1540-PIT-7422 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5074 | PGS FROM WHB TO JUG VALVE | 78"-SOX-1540-2106-304SS-HC- | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7422 | NEW | 1540-PI-7422 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | PGS FROM WHB TO JUG VALVE | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7422 | NEW | 1540-FI-7422 | FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5074 | PURGE FOR PIT-7422 | ------ | 1540-HX-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7490 | NEW | 1540-FE-7490 | FLOW ELEMENT - ORIFICE PLATE | 1540-PR-PID-0000-EXP-5074 | WHB CONTINUOUS BLOWDOWN | 2"-RCW-1540-4159-CDB-HC- | 1540-HX-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7490 | NEW | 1540-FIT-7490 | FLOW TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5074 | WHB CONTINUOUS BLOWDOWN | ------ | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-7490 | NEW | 1540-FI-7490 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | WHB CONTINUOUS BLOWDOWN | ------ | 1540-HX-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7641 | NEW | 1540-TW-7641 | VENDOR SUPPLY THERMOWELL | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7641 | NEW | 1540-TI-7641 | VENDOR SUPPLY TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7650 | NEW | 1540-LG-7650 | VENDOR SUPPLY LEVEL GAUGE - SIGHT GLASS | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7610 | NEW | 1540-PI-7610 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7680 | NEW | 1540-PSV-7680 | PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7640 | NEW | 1540-LIT-7640 | LEVEL TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7640 | NEW | 1540-LIC-7640 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7640 | NEW | 1540-LAL-7640 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7640 | NEW | 1540-LAH-7640 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7640 | NEW | 1540-LY-7640 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | ------ | 1540-PV-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7640 | NEW | 1540-LCV-7640 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5076 | PRESSURIZED BOILER BLOWDOWN TK | 2"-RCW-1540-4180-CBO-HC- | 1540-PV-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7611 | NEW | 1540-PI-7611 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5076 | ATMOSPHERIC BLOWDOWN TK PRESS | ------ | 1540-TK-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7630 | NEW | 1540-TW-7630 | VENDOR SUPPLY THERMOWELL | 1540-PR-PID-0000-EXP-5076 | ATMOSPHERIC BOILER BLOWDOWN TK | ------ | 1540-TK-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7630 | NEW | 1540-TI-7630 | VENDOR SUPPLY TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5076 | ATMOSPHERIC BOILER BLOWDOWN TK | ------ | 1540-TK-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7651 | NEW | 1540-LG-7651 | VENDOR SUPPLY LEVEL GAUGE - SIGHT GLASS | 1540-PR-PID-0000-EXP-5076 | ATMOSPHERIC BOILER BLOWDOWN TK | ------ | 1540-TK-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LIT-7655 | LEVEL TRANSMITTER - GWR | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LI-7655 | DCS INDICATION | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LSL-7655 | INTLK | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LSH-7655 | INTLK | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LAH-7655 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LAHH-7655 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LAL-7655 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-7655 | NEW | 1540-LALL-7655 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7656 | NEW | 1540-PI-7656 | PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP PUMP DIACHARGE | 2"-RCW-1540-4184-CBM-FP-ET | 1540-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | YES
1500 | 1540 | CONTACT SECTION | 1540-H-7657 | NEW | 1540-HS-7657 | MOTOR CONTROL | 1540-PR-PID-0000-EXP-5076 | BOILER BLOWDOWN SUMP PUMP | ------ | 1540-PP-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1540 | N | SWRK | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7821 | NEW | 1540-TW-7821 | THERMOWELL | 1540-PR-PID-0000-EXP-5078 | PGS FROM CONV PASS 1 TO HP SH 1B | 84"-SOX-1540-2110-304SS-HC- | 1540-HX-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TE-7810 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | 14"-HPS-1540-4190-AEB-HC- | 1540-HX-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7821 | NEW | 1540-TIT-7821 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5078 | PGS FROM CONV PASS 1 TO HP SH 1B | ------ | 1540-HX-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7821 | NEW | 1540-TI-7821 | DCS INDICATION | 1540-PR-PID-0000-EXP-5078 | PGS FROM CONV PASS 1 TO HP SH 1B | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7821 | NEW | 1540-TAH-7821 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | PGS FROM CONV PASS 1 TO HP SH 1B | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-ZI-4822 | DCS INDICATION | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-ZT-4822 | POSITION TRANSMITTER | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-ZP-007 | Vendor | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-HS-4822 | LOCAL START/STOP SWITCH | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-ZP-007 | Vendor | N/A | DO | N/A | 24V | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-4822A | NEW | 1540-HS-4822A | LOCAL START/STOP SWITCH | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-ZP-007 | Vendor | N/A | DO | N/A | 24V | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TCV-4822A | JUG VALVE | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | 78"-SOX-1540-2118-304SS-HC- | 1540-ZP-007 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TCV-4822B | METALLIC DAMPER | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | 78"-SOX-1540-2112-304SS-HC- | 1540-HX-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TY-4822A | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-TY-4822B | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-HX-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-FI-4822A | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5078 | PURGE FOR TCV-4822A | ------ | 1540-ZP-007 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-FI-4822B | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1540-PR-PID-0000-EXP-5078 | PURGE FOR TCV-4822B | ------ | 1540-HX-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-4822 | NEW | 1540-UY-4822 | DCS CALCULATION | 1540-PR-PID-0000-EXP-5078 | PGS FROM WHB TO JUG VALVE | ------ | 1540-ZP-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7835 | NEW | 1540-TW-7835 | VENDOR SUPPLY THERMOWELL | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM SH 4A TO SH 1B | ------ | 1540-HX-003 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7835 | NEW | 1540-TI-7835 | VENDOR SUPPLY TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM SH 4A TO SH 1B | ------ | 1540-HX-003 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7815 | NEW | 1540-PI-7815 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM SH 4A TO SH 1B | ------ | 1540-HX-004 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7836 | NEW | 1540-TW-7836 | VENDOR SUPPLY THERMOWELL | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM SH 1B TO TG SET | ------ | 1540-HX-004 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7836 | NEW | 1540-TI-7836 | VENDOR SUPPLY TEMPERATURE GAUGE | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM SH 1B TO TG SET | ------ | 1540-HX-004 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7816 | NEW | 1540-PI-7816 | VENDOR SUPPLY PRESSURE GAUGE | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM SH 1B TO TG SET | ------ | 1540-HX-004 | Vendor | N/A | N/A | N/A | N/A | PECS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TW-7810 | THERMOWELL | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | 14"-HPS-1540-4190-AEB-HC- | 1540-HX-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7823 | NEW | 1540-TE-7823 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5078 | PGS FROM HP SH 1B TO JUG VALVE | 78"-SOX-1540-2112-304SS-HC- | 1540-HX-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TIT-7810 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | ------ | 1540-HX-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TIC-7810 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TAL-7810 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7810 | NEW | 1540-TAH-7810 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TW-7660 | THERMOWELL | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | 6"-RCW-1540-4181-CBO-PP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TE-7660 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | 6"-RCW-1540-4181-CBO-PP- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TIT-7660 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TIC-7660 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TAH-7660 | DCS ALARM | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TY-7660 | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7660 | NEW | 1540-TCV-7660 | CONTROL VALVE | 1540-PR-PID-0000-EXP-5076 | RAW WATER TO BOILER BLOWDOWN TANK | 2"-RAW-1540-474-CBA-FP-ET | N/A | 5022 | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7881 | NEW | 1540-PSV-7881 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5078 | HP STEAM FROM HP SH 1B TO TG SET | 14"-HPS-1540-4190-AEB-HC- | 1540-HX-003 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806 | NEW | 1540-PIT-7806 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | 14"-HPS-1540-4190-AEB-HC- | 1540-HX-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806 | NEW | 1540-PIC-7806 | DCS INDICATION AND CONTROL | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806 | NEW | 1540-PAL-7806 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806 | NEW | 1540-PAH-7806 | DCS ALARM | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806A | NEW | 1540-PY-7806A | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | ------ | 1540-HX-003 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806A | NEW | 1540-PCV-7806A | CONTROL VALVE | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | 14"-HPS-1540-4190-AEB-HC- | 1540-HX-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806B | NEW | 1540-PY-7806B | SMART VALVE POSITIONER | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | ------ | 1540-HX-003 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-7806B | NEW | 1540-PCV-7806B | CONTROL VALVE PART OF SILENCER | 1540-PR-PID-0000-EXP-5078 | HP STEAM TO TG SET | 12"-HPS-1540-6539-AEA-HC- | 1540-HX-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7823 | NEW | 1540-TW-7823 | THERMOWELL | 1540-PR-PID-0000-EXP-5078 | PGS FROM HP SH 1B TO JUG VALVE | 78"-SOX-1540-2112-304SS-HC- | 1540-HX-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-8025 | NEW | 1540-TE-8025 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7823 | NEW | 1540-TIT-7823 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5078 | PGS FROM HP SH 1B TO JUG VALVE | ------ | 1540-HX-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-001 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7823 | NEW | 1540-TI-7823 | DCS INDICATION | 1540-PR-PID-0000-EXP-5078 | PGS FROM HP SH 1B TO JUG VALVE | ------ | 1540-HX-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7887 | NEW | 1540-XB-7887 | VENT SILENCER | 1540-PR-PID-0000-EXP-5078 | HP SH 1B HP STEAM VENT | ------ | 1540-HX-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-8026 | NEW | 1540-FE-8026 | FLOW ELEMENT - AVERAGING PITOT TUBE | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-8026 | NEW | 1540-FIT-8026 | FLOW TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-F-8026 | NEW | 1540-FI-8026 | DCS INDICATION | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-F-8026 | NEW | 1540-FX-8026 | DCS CALCULATION | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-8025 | NEW | 1540-TW-8025 | THERMOWELL | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2430 | NEW | 1550-TE-2430 | TEMPERATURE ELEMENT - TC TYPE K | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | 12"-CLW-1550-5102-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-8025 | NEW | 1540-TIT-8025 | TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-8025 | NEW | 1540-TI-8025 | DCS INDICATION | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-8024 | NEW | 1540-PIT-8024 | PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-8024 | NEW | 1540-PI-8024 | DCS INDICATION | 1540-PR-PID-0000-EXP-5080 | LP STEAM DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1107 | NEW | 1540-PI-1107 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP LUBE OIL PRESS LL SHUTDOWN | ------ | 1540-GB-001 | EXP | PLC | AI-HART-S | DCS | 4-20mA HART | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1107 | NEW | 1540-PALL-1107 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP LUBE OIL PRESS LL SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1061 | NEW | 1540-XS-1061 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP READY TO START | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-H-1061 | NEW | 1540-HIC-1073 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | COMP SPEED CONTROL | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-H-1071 | NEW | 1540-HS-1071 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | DCS SHUTDOWN COMP | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | PLC | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-E-41061 | NEW | 1540-ESD-1061 | DCS INITIATED SHUT-DOWN | 1540-PR-PID-0000-EXP-5040 | EMERGENCY SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1020 | NEW | 1540-TAH-1020 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP COMMON H BEARING TEMPERATURE ALOARM | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1020 | NEW | 1540-TAHH-1020 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP COMMON HH BEARING TEMPERATURE SHUTDOWN | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1060 | NEW | 1540-VAHH-1060 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP COMMON HH VIBRATION SHUTDOWN | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1060 | NEW | 1540-VAH-1060 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP COMMON H VIBRATION ALARM | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-002 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1075 | NEW | 1540-HS-1094 | PUSHBUTTON | 1540-PR-PID-0000-EXP-5040 | MAIN COMP SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | DO-S | PLC | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1075 | NEW | 1540-HS-1115 | PUSHBUTTON | 1540-PR-PID-0000-EXP-5040 | MAIN COMP SHUTDOWN | ------ | 1540-GB-001 | EXP | DCS | DO-S | PLC | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1075 | NEW | 1540-XS-1022 | OPERATOR INITIATED DCS CONTROL | 1540-PR-PID-0000-EXP-5040 | MAIN COMP START | ------ | 1540-GB-001 | EXP | DCS | DI-S | PLC | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1075 | NEW | 1540-XS-1023 | OPERATOR INITIATED DCS CONTROL | 1540-PR-PID-0000-EXP-5040 | MAIN COMP START | ------ | 1540-GB-001 | EXP | DCS | DI-S | PLC | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1075 | NEW | 1540-HS-1021 | OPERATOR INITIATED DCS CONTROL | 1540-PR-PID-0000-EXP-5040 | MAIN COMP START | ------ | 1540-GB-001 | EXP | DCS | DO-S | PLC | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1075 | NEW | 1540-XS-1075 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP SPEED START-UP PERMISSIVE | ------ | 1540-GB-001 | EXP | DCS | DO-S | PLC | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1079 | NEW | 1540-XI-1079 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP SPEED RPM | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-1077 | NEW | 1540-XS-1077 | DCS INDICATION | 1540-PR-PID-0000-EXP-5040 | MAIN COMP RUNNING/STOP STATUS | ------ | 1540-GB-001 | EXP | PLC | DI-S | DCS | 24V | DCS | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1280 | NEW | 1540-PSV-1280 | PRESSURE RELIEF VALVE | 1540-PR-PID-0000-EXP-5040 | CW SUPPLY TO LUBE OIL SYS | 4"-CLW-1540-2347-CBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-R-1281 | NEW | 1540-RO-1281 | RESTRICTION ORIFICE | 1540-PR-PID-0000-EXP-5040 | CW SUPPLY TO LUBE OIL SYS | 4"-CLW-1540-5114-CBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LIT-2215 | LEVEL TRANSMITTER - RADAR | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LI-2215 | PROCESS INDICATOR | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | N/A | N/A | N/A | 24V | FLD-OFFLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LIC-2215 | DCS INDICATION AND CONTROL | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LSLL-2215 | INTLK | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LAH-2215 | DCS ALARM | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LAL-2215 | DCS ALARM | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LY-2215 | SMART VALVE POSITIONER | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | ------ | 1550-CT-001/002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-L-2215 | NEW | 1550-LCV-2215 | CONTROL VALVE | 1550-PR-PID-0000-EXP-5122 | CT RESEVOIR | 3"-PCD-1550-0101-SBA-FP-ET | 1550-CT-001/002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | YES
1500 | 1550 | COOLING WATER SYSTEM | 1550-V-2201 | NEW | 1550-VSH-2201 | VIBRATION SWITCH | 1550-PR-PID-0000-EXP-5122 | SA1 CT FAN | ------ | 1550-CT-001 | EXP | DCS | DI | RIO | 24V | FLD-EQUIP | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-V-2201 | NEW | 1550-VAH-2201 | DCS ALARM | 1550-PR-PID-0000-EXP-5122 | SA1 CT FAN | ------ | 1550-CT-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-H-2201 | NEW | 1550-HS-2201 | MOTOR CONTROL | 1550-PR-PID-0000-EXP-5122 | SA1 CT FAN | ------ | 1550-CT-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-H-2210 | NEW | 1550-HS-2210 | MOTOR CONTROL | 1550-PR-PID-0000-EXP-5122 | SA1 CT PUMP | ------ | 1550-PP-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1550 | N | SWRK | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-H-2212 | NEW | 1550-HS-2212 | MOTOR CONTROL | 1550-PR-PID-0000-EXP-5122 | SA1 CT PUMP | ------ | 1550-PP-002 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1550 | N | SWRK | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-2211 | NEW | 1550-PI-2211 | PRESSURE GAUGE | 1550-PR-PID-0000-EXP-5122 | SA1 CT PUMP | 12"-CLW-1550-5102-CBA-- | 1550-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-2213 | NEW | 1550-PI-2213 | PRESSURE GAUGE | 1550-PR-PID-0000-EXP-5122 | SA1 CT PUMP | 12"-CLW-1550-5120-CBA-- | 1550-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2217 | NEW | 1550-AE-2217 | ANALYZER SENSOR - CONDUCTIVITY | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | 12"-CLW-1550-5102-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2217 | NEW | 1550-AIT-2217 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2217 | NEW | 1550-AIC-2217 | DCS INDICATION AND CONTROL | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART-S | DCS | 4-20mA HART | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2217 | NEW | 1550-AAH-2217 | DCS ALARM | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2217 | NEW | 1550-AY-2217 | SMART VALVE POSITIONER | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2217 | NEW | 1550-ACV-2217 | CONTROL VALVE | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | 2"-CLW-1550-5108-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | YES
1500 | 1550 | COOLING WATER SYSTEM | 1550-F-2218 | NEW | 1550-FE-2218 | FLOW ELEMENT - ORIFICE PLATE | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | 12"-CLW-1550-5102-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-F-2218 | NEW | 1550-FIT-2218 | FLOW TRANSMITTER - D/P | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-F-2218 | NEW | 1550-FI-2218 | DCS INDICATION | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-F-2218 | NEW | 1550-FALL-2218 | DCS ALARM | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-F-2218 | NEW | 1550-FSL-2218 | INTLK | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-F-2218 | NEW | 1550-FAL-2218 | DCS ALARM | 1550-PR-PID-0000-EXP-5122 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-R-2222 | NEW | 1550-RO-2222 | RESTRICTION ORIFICE | 1550-PR-PID-0000-EXP-5122 | CW HEADER | 1"-CLW-1550-5129-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2430 | NEW | 1550-TW-2430 | THERMOWELL | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | 12"-CLW-1550-5102-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2432 | NEW | 1550-TE-2432 | TEMPERATURE ELEMENT - TC TYPE K | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | 12"-CLW-1550-5116-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2430 | NEW | 1550-TIT-2430 | TEMPERATURE INDICATING TRANSMITTER | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2430 | NEW | 1550-TI-2430 | DCS INDICATION | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2430 | NEW | 1550-TSH-2430 | INTLK | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2430 | NEW | 1550-TSL-2430 | INTLK | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2432 | NEW | 1550-TW-2432 | THERMOWELL | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | 12"-CLW-1550-5116-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2620 | NEW | 1560-TE-2620 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | 8"-RAW-1560-0100-CBA-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2432 | NEW | 1550-TIT-2432 | TEMPERATURE INDICATING TRANSMITTER | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2432 | NEW | 1550-TI-2432 | DCS INDICATION | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-T-2432 | NEW | 1550-TAH-2432 | DCS ALARM | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-2431 | NEW | 1550-PI-2431 | PRESSURE GAUGE | 1550-PR-PID-0000-EXP-5124 | CW SUPPLY HEADER | 12"-CLW-1550-5102-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-2433 | NEW | 1550-PI-2433 | PRESSURE GAUGE | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | 12"-CLW-1550-5116-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2461 | NEW | 1550-AE-2461 | ANALYZER SENSOR - CONDUCTIVITY | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | 12"-CLW-1550-5116-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2461 | NEW | 1550-AIT-2461 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2461 | NEW | 1550-AI-2461 | DCS INDICATION | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2461 | NEW | 1550-AAH-2461 | DCS ALARM | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2461 | NEW | 1550-ADI-2461 | DCS INDICATION | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-A-2461 | NEW | 1550-ADAH-2461 | DCS ALARM | 1550-PR-PID-0000-EXP-5124 | CW RETURN HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3000 | NEW | 1550-PIT-3000 | PRESSURE TRANSMITTER | 1550-PR-PID-0000-EXP-5130 | INSTRUMENT AIR RECEIVER | ------ | 1550-AR-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3000 | NEW | 1550-PI-3000 | DCS INDICATION | 1550-PR-PID-0000-EXP-5130 | INSTRUMENT AIR RECEIVER | ------ | 1550-AR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3000 | NEW | 1550-PAL-3000 | DCS ALARM | 1550-PR-PID-0000-EXP-5130 | INSTRUMENT AIR RECEIVER | ------ | 1550-AR-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3001 | NEW | 1550-PSV-3001 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1550-PR-PID-0000-EXP-5130 | INSTRUMENT AIR RECEIVER | ------ | 1550-AR-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3002 | NEW | 1550-PI-3002 | PRESSURE GAUGE | 1550-PR-PID-0000-EXP-5130 | INSTRUMENT AIR RECEIVER | ------ | 1550-AR-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3200 | NEW | 1550-PIT-3200 | PRESSURE TRANSMITTER | 1550-PR-PID-0000-EXP-5132 | PLANT AIR RECEIVER | ------ | 1550-AR-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1550 | N | 1550-JBP-001 | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3200 | NEW | 1550-PI-3200 | DCS INDICATION | 1550-PR-PID-0000-EXP-5132 | PLANT AIR RECEIVER | ------ | 1550-AR-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3200 | NEW | 1550-PAL-3200 | DCS ALARM | 1550-PR-PID-0000-EXP-5132 | PLANT AIR RECEIVER | ------ | 1550-AR-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3201 | NEW | 1550-PSV-3201 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1550-PR-PID-0000-EXP-5132 | PLANT AIR RECEIVER | ------ | 1550-AR-002 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3202 | NEW | 1550-PI-3202 | PRESSURE GAUGE | 1550-PR-PID-0000-EXP-5132 | PLANT AIR RECEIVER | ------ | 1550-AR-002 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1550 | N | N/A | NO
1500 | 1550 | COOLING WATER SYSTEM | 1550-P-3203 | NEW | 1550-PRV-3203 | SELF REGULATING VALVE | 1550-PR-PID-0000-EXP-5132 | PLANT AIR RECEIVER | 3"-INA-1550-0165-CBK-- | 1550-AR-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1550 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-2600 | NEW | 1560-PIT-2600 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | 8"-RAW-1560-0100-CBA-FP-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-2600 | NEW | 1560-PI-2600 | DCS INDICATION | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-2600 | NEW | 1560-PAL-2600 | DCS ALARM | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2620 | NEW | 1560-TW-2620 | THERMOWELL | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | 8"-RAW-1560-0100-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3815 | NEW | 1560-TE-3815 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | 6"-TRW-1560-0192-SBA-FP- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2620 | NEW | 1560-TIT-2620 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2620 | NEW | 1560-TI-2620 | DCS INDICATION | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2902 | NEW | 1560-TE-2902 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | 8"-RAW-1560-0100-CBA-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2902 | NEW | 1560-TW-2902 | THERMOWELL | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | 8"-RAW-1560-0100-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2902 | NEW | 1560-TIT-2902 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2902 | NEW | 1560-TIC-2902 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-2902 | NEW | 1560-TI-2902 | DCS INDICATION | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2670 | NEW | 1560-FE-2670 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | 8"-RAW-1560-0100-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2670 | NEW | 1560-FIT-2670 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | 8"-RAW-1560-100-CBA-FP- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-2670 | NEW | 1560-FI-2670 | DCS INDICATION | 1560-PR-PID-0000-EXP-5126 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3401 | NEW | 1560-LIT-3401 | LEVEL TRANSMITTER - RADAR | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | ------ | 1560-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3401 | NEW | 1560-LI-3401 | DCS INDICATION | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | ------ | 1560-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3401 | NEW | 1560-LAL-3401 | DCS ALARM | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | ------ | 1560-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3401 | NEW | 1560-LAH-3401 | DCS ALARM | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | ------ | 1560-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3401 | NEW | 1560-LSLL-3401 | INTLK | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | ------ | 1560-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-2901 | NEW | 1560-LIT-2901 | LEVEL TRANSMITTER - GWR | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | 1560-TK-005 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-2901 | NEW | 1560-LIC-2901 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | 1560-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-2901 | NEW | 1560-LSLL-2901 | INTLK | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | 1560-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-2901 | NEW | 1560-LSHH-2901 | INTLK | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | 1560-TK-005 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-LY-2901 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-LCV-2901 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK | 3"-TRW-1560-9827-SBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3406 | NEW | 1560-PI-3406 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | 6"-TRW-1560-0239-SBA-FP- | 1560-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3407 | NEW | 1560-PI-3407 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5134 | TW STOR TK | 6"-TRW-1560-0240-SBA-FP- | 1560-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-2910 | NEW | 1560-HS-2910 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK PUMP | ------ | 1560-PP-021 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-2920 | NEW | 1560-HS-2920 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK PUMP | ------ | 1560-PP-022 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-3405 | NEW | 1560-HS-3405 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5134 | TW EXPORT PUMP | ------ | 1560-PP-006 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-3408 | NEW | 1560-HS-3408 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5134 | TW EXPORT PUMP | ------ | 1560-PP-007 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3409 | NEW | 1560-FE-3409 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | 6"-TRW-1560-0239-SBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3409 | NEW | 1560-FIT-3409 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-3420 | NEW | 1560-RO-3420 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5134 | TW STOR TK TO CIP SYS | 3"-TRW-1560-9802-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-3406 | NEW | 1560-RO-3406 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5134 | TW PUMP DISCH RECYCLE | 1"-TRW-1560-0240-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-2911 | NEW | 1560-PI-2911 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK DISCH | 3"-TRW-1560-9826-SBA-- | 1560-PP-021 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-2921 | NEW | 1560-PI-2921 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK DISCH | 3"-TRW-1560-9827-SBA-- | 1560-PP-022 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-2930 | NEW | 1560-RO-2930 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5129 | RECOVERY TK DISCH RECYCLE | 3"-TRW-1560-9827-SBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3409 | NEW | 1560-FI-3409 | DCS INDICATION | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3430 | NEW | 1560-PIT-3430 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | 6"-TRW-1560-0239-SBA-FP- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3430 | NEW | 1560-PIC-3430 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3430 | NEW | 1560-PY-3430 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3430 | NEW | 1560-PCV-3430 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5134 | TW TO LITHIUM PROCESSING | 6"-TRW-1560-0239-SBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LIT-3601 | LEVEL TRANSMITTER - GWR | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LI-3601 | DCS INDICATION | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LI-3601A | DCS INDICATION | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LIC-3601A | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LALL-3601 | DCS INDICATION | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LAH-3601 | INTLK | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LSH-3601 | DCS INDICATION | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LSL-3601 | INTLK | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LAHH-3601 | DCS INDICATION | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LY-3601 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-3601 | NEW | 1560-LCV-3601 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | 8"-RCW-1560-5128-CA-FP- | N/A | 5029 | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3601 | NEW | 1560-FE-3601 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | N/A | N/A | N/A | N/A | N/A | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3601 | NEW | 1560-FIT-3601 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | AI-HART | DCS | 4-20mA HART | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3601 | NEW | 1560-FIC-3601 | DCS ALARM | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3601 | NEW | 1560-FSLL-3601 | DCS ALARM | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3601 | NEW | 1560-FAL-3601 | DCS ALARM | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3601 | NEW | 1560-FAH-3601 | DCS ALARM | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-3602 | NEW | 1560-HS-3602A | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP PUMP | ------ | 1560-PP-012 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-3602 | NEW | 1560-HS-3602B | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP PUMP (STANDBY) | ------ | 1560-PP-013 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3610 | NEW | 1560-PI-3610 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP PUMP DISCH | 8"-RAW-1560-5128-CBA-- | 1560-PP-012 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3611 | NEW | 1560-PI-3611 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP PUMP (STANDBY) DISCH | 8"-RAW-1560-0189-CBA-- | 1560-PP-013 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3632 | NEW | 1560-PIC-3632 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5131 | RAW WATER TO MULTIMEDIA FLTS | ------ | 1560-FL-001/002/003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3632 | NEW | 1560-PIT-3632 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5131 | RAW WATER TO MULTIMEDIA FLTS | 8"-RAW-1560-0105-CBA-FP- | 1560-FL-001/002/003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3632 | NEW | 1560-PAH-3632 | DCS ALARM | 1560-PR-PID-0000-EXP-5131 | RAW WATER TO MULTIMEDIA FLTS | ------ | 1560-FL-001/002/003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3632 | NEW | 1560-PAL-3632 | DCS ALARM | 1560-PR-PID-0000-EXP-5131 | RAW WATER TO MULTIMEDIA FLTS | ------ | 1560-FL-001/002/003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3632 | NEW | 1560-PY-3632 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5131 | RAW WATER TO MULTIMEDIA FLTS | ------ | 1560-FL-001/002/003 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3632 | NEW | 1560-PCV-3632 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5131 | RAW WATER TO MULTIMEDIA FLTS | 8"-RAW-1560-0105-CBA-FP- | 1560-FL-001/002/003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-L-6840 | NEW | 1540-LSH-6840 | INTLK | 1540-PR-PID-0000-EXP-5068 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-6840 | NEW | 1560-LY-6840 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5138 | DEAERATOR STOR LEVEL | ------ | 1540-PV-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-6840 | NEW | 1560-LCV-6840 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5138 | DEAERATOR STOR LEVEL | 6"-TRW-1560-0192-SBA-FP- | 1540-PV-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3800 | NEW | 1560-PIT-3800 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | 6"-TRW-1560-0192-SBA-FP-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3800 | NEW | 1560-PI-3800 | DCS INDICATION | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3800 | NEW | 1560-PAL-3800 | DCS ALARM | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3800 | NEW | 1560-PAH-3800 | DCS ALARM | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-3809 | NEW | 1560-RO-3809 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5138 | CW HEADER | 1"-TRW-1560-0194-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3815 | NEW | 1560-TW-3815 | THERMOWELL | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | 6"-TRW-1560-0192-SBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3911 | NEW | 1560-TE-3911 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3815 | NEW | 1560-TIT-3815 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3815 | NEW | 1560-TI-3815 | DCS INDICATION | 1560-PR-PID-0000-EXP-5138 | TW TO BFW PREHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TE-3102 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5131 | RAW WATER HEADER | 6"-TRW-1560-0192-SBA-FP- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TW-3102 | THERMOWELL | 1560-PR-PID-0000-EXP-5131 | RAW WATER HEADER | 6"-TRW-1560-0192-SBA-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TIT-3102 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5131 | RAW WATER HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TIC-3102 | DCS INDICATION | 1560-PR-PID-0000-EXP-5131 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TAH-3102 | DCS INDICATION | 1560-PR-PID-0000-EXP-5131 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TAL-3102 | DCS INDICATION | 1560-PR-PID-0000-EXP-5131 | RAW WATER HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TY-3102A | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5136 | RAW WATER HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TCV-3102A | CONTROL VALVE | 1560-PR-PID-0000-EXP-5136 | RAW WATER HEADER | 8"-LCD-1560-0401-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TY-3102B | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5136 | RAW WATER HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3102 | NEW | 1560-TCV-3102B | CONTROL VALVE | 1560-PR-PID-0000-EXP-5136 | RAW WATER HEADER | 8"-RAW-1560-6125-CBO-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3810 | NEW | 1560-PI-3810 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5138 | TW PUMP | 6"-TRW-1560-0192-SBA-FP- | 1560-PP-010 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3811 | NEW | 1560-PI-3811 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5138 | TW PUMP (STANDBY) | 6"-TRW-1560-0193-SBA-FP- | 1560-PP-011 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-3809A | NEW | 1560-HS-3809A | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5138 | TW PUMP | ------ | 1560-PP-010 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-3809B | NEW | 1560-HS-3809B | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5138 | TW PUMP (STANDBY) | ------ | 1560-PP-011 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3900 | NEW | 1560-FE-3900 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5139 | TREATED WATER TO COND. HEADER | 3"-TRW-1560-5460-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3900 | NEW | 1560-FIT-3900 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5139 | TREATED WATER TO COND. HEADER | 3"-TRW-1560-5460-SBA-FP-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3900 | NEW | 1560-FI-3900 | DCS INDICATION | 1560-PR-PID-0000-EXP-5139 | TREATED WATER TO COND. HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-PIT-3901 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-PIC-3901 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-PY-3901A | CONTROL VALVE | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-PCV-3901A | CONTROL VALVE | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-TRW-1560-5460-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-PY-3901B | CONTROL VALVE | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3901 | NEW | 1560-PCV-3901B | CONTROL VALVE | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-5461-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3910 | NEW | 1560-PIT-3910 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-3910 | NEW | 1560-PI-3910 | DCS INDICATION | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-3910 | NEW | 1560-PAL-3910 | DCS ALARM | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3911 | NEW | 1560-TW-3911 | THERMOWELL | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3914 | NEW | 1560-TE-3914 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3911 | NEW | 1560-TIT-3911 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3911 | NEW | 1560-TI-3911 | DCS INDICATION | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3912 | NEW | 1560-FE-3912 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3912 | NEW | 1560-FIT-3912 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3912 | NEW | 1560-FI-3912 | DCS INDICATION | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3914 | NEW | 1560-TW-3914 | THERMOWELL | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-9441-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6003 | NEW | 1560-TE-6003 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | 14"-HPS-1540-4190-AEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3914 | NEW | 1560-TIT-3914 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-3914 | NEW | 1560-TI-3914 | DCS INDICATION | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3920 | NEW | 1560-FE-3920 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | 3"-PCD-1560-5461-SBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3920 | NEW | 1560-FIT-3920 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-3920 | NEW | 1560-FI-3920 | DCS INDICATION | 1560-PR-PID-0000-EXP-5139 | PROCESS COND. DISTRIBUTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6001 | NEW | 1560-PIT-6001 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | 2"-BFW-1540-4129-CEA-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6001 | NEW | 1560-PI-6001 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6002 | NEW | 1560-PIT-6002 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | 14"-HPS-1540-4190-AEA-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6002 | NEW | 1560-PI-6002 | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6002 | NEW | 1560-PIC-6002 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-6001 | NEW | 1560-RO-6001 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5160 | HP STEAM FROM HP SH 1B | 3/4"-HCD-1560-9624-AEA-PP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6408 | NEW | 1560-FE-6408 | FLOW ELEMENT - AVERAGING PITOT TUBE | 1560-PR-PID-0000-EXP-5160 | HP STEAM FROM HP SH 1B | 14"-HPS-1540-4190-AEA-HC- | N/A | EXP | DCS | E-T | N/A | E-T | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6004 | NEW | 1560-FE-6004 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | 14"-HPS-1540-4190-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FIELD-INLINE | 1560 | N | N/A
1500 | 1560 | TURBO GENERATOR | 1560-F-6004 | NEW | 1560-FIT-6004 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6004 | NEW | 1560-FI-6004A | DCS INDICATION | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6004 | NEW | 1560-FI-6004B | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6004 | NEW | 1560-FY-6004 | DCS CALCULATION | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6003 | NEW | 1560-TW-6003 | THERMOWELL | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | 14"-HPS-1540-4190-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6009 | NEW | 1560-TE-6009 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5160 | CW SUPPLY TO TG SET | 8"-CLW-1560-5115-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6003 | NEW | 1560-TIT-6003 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6003 | NEW | 1560-TI-6003A | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6003 | NEW | 1560-TI-6003B | DCS INDICATION | 1560-PR-PID-0000-EXP-5159 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6009 | NEW | 1560-TW-6009 | THERMOWELL | 1560-PR-PID-0000-EXP-5160 | CW SUPPLY TO TG SET | 8"-CLW-1560-5115-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6006 | NEW | 1560-TE-6006 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5160 | CW RETURN FROM TG SET | 8"-CLW-1560-2378-CBA-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6009 | NEW | 1560-TIT-6009 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | CW SUPPLY TO TG SET | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6009 | NEW | 1560-TI-6009 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | CW SUPPLY TO TG SET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6009 | NEW | 1560-TAL-6009 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | CW SUPPLY TO TG SET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6005 | NEW | 1560-PI-6005 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5160 | CW SUPPLY TO TG SET | 8"-CLW-1560-5115-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6006 | NEW | 1560-TW-6006 | THERMOWELL | 1560-PR-PID-0000-EXP-5160 | CW RETURN FROM TG SET | 8"-CLW-1560-2378-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6012 | NEW | 1560-TE-6012 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 4"-LPS-1560-8742-AEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6006 | NEW | 1560-TIT-6006 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | CW RETURN FROM TG SET | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6006 | NEW | 1560-TI-6006 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | CW RETURN FROM TG SET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6007 | NEW | 1560-PI-6007 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5160 | CW RETURN FROM TG SET | 8"-CLW-1560-2378-CBA-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6011 | NEW | 1560-PIT-6011 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 4"-MPS-1560-6109-CBB-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6011 | NEW | 1560-PIC-6011 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6011 | NEW | 1560-PY-6011 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6011 | NEW | 1560-PCV-6011 | SPRAY DESUPERHEATER CONTROL VALVE | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH LETDOWN | 4"-HPS-1560-8742-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6023 | NEW | 1560-PSV-6023 | PRESSURE RELIEF VALVE | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 4"-MPS-1560-6108-ACA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6012 | NEW | 1560-TW-6012 | THERMOWELL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 4"-LPS-1560-8742-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TE-6014 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | 4"-LPS-1560-6109-CBO-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6012 | NEW | 1560-TIT-6012 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6012 | NEW | 1560-TI-6012 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6020 | NEW | 1560-FE-6020 | FLOW ELEMENT - AVERAGING PITOT TUBE | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | 4"-LPS-1560-6109-CBO-HC- | N/A | EXP | DCS | E-T | N/A | E-T | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6020 | NEW | 1560-FIT-6020 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6020 | NEW | 1560-FI-6020 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6044 | NEW | 1560-FE-6044 | FLOW ELEMENT - AVERAGING PITOT TUBE | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | 4"-HPS-1560-8742-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6044 | NEW | 1560-FIT-6044 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6044 | NEW | 1560-FI-6044 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6015 | NEW | 1560-PIT-6015 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | 4"-LPS-1560-6109-CBO-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6015 | NEW | 1560-PI-6015 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TW-6014 | THERMOWELL | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | 4"-LPS-1560-6109-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TE-6018 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TIT-6014 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TIC-6014 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TAH-6014 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | BFW TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TY-6014 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5160 | HP to IP SPRAY WATER CONTROL VALVE | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6014 | NEW | 1560-TCV-6014 | SPRAY DESUPERHEATER CONTROL VALVE | 1560-PR-PID-0000-EXP-5160 | HP to IP SPRAY WATER CONTROL VALVE | 2"-BFW-1540-4129-CEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-6301 | NEW | 1560-RO-6301 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | 1"-LCD-1560-9602-CBB-HC- | 1560-TG-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6301 | NEW | 1560-XV-6301 | ON/OFF VALVE | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | 1"-LCD-1560-9602-CBO-HC- | 1560-TG-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6301 | NEW | 1560-XEV-6301 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | ------ | 1560-TG-001 | EXP | DCS | DCS | DCS | N/A | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6301 | NEW | 1560-ZIC-6301 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | ------ | N/A | EXP | DCS | DI | DCS | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6301 | NEW | 1560-ZIO-6301 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | ------ | N/A | EXP | DCS | DI | DCS | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6301 | NEW | 1560-ZAO-6301 | DCS INDICATION | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6301 | NEW | 1560-ZAC-6301 | DCS INDICATION | 1560-PR-PID-0000-EXP-5163 | TG EXTRACTION LINE DRAIN | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6426 | NEW | 1560-TW-6426 | THERMOWELL | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | 2"-HPS-1560-6105-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6671 | NEW | 1560-TE-6671 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6426 | NEW | 1560-TIT-6426 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6426 | NEW | 1560-TI-6426 | DCS INDICATION | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6425 | NEW | 1560-PIT-6425 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | 2"-HPS-1560-6105-AEA-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6425 | NEW | 1560-PI-6425 | DCS INDICATION | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | ------ | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6425 | NEW | 1560-PI-6425 | DCS INDICATION | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6024 | NEW | 1560-PSV-6024 | PRESSURE RELIEF VALVE | 1560-PR-PID-0000-EXP-5165 | 70 PSIG STEAM TO DISTRIBUTION HEADER | 16"-LPS-1560-6535-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6025 | NEW | 1560-PSV-6025 | PRESSURE RELIEF VALVE | 1560-PR-PID-0000-EXP-5160 | LPS FROM STG | 14"-LPS-1560-563-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9339 | NEW | 1560-TW-9339 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | ACC VACUUM PUMP INLET | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9339 | NEW | 1560-TE-9339 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5177 | ACC VACUUM PUMP INLET | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9339 | NEW | 1560-TIT-9339 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5177 | ACC VACUUM PUMP INLET | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9339 | NEW | 1560-TIA-9339 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | ACC VACUUM PUMP INLET | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9339 | NEW | 1560-TIAH-9339 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | ACC VACUUM PUMP INLET | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TW-9353 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TE-9353 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TIT-9353 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TIA-9353 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TIAH-9353 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TIAL-9353 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9353 | NEW | 1560-TSHH-9353 | INTLK | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6401 | NEW | 1560-TW-6401 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5164 | 1560-TK-006 EXTERNAL COND COLLECTION TANK | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6401 | NEW | 1560-TI-6401 | VENDOR SUPPLY BI-METALLIC TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5164 | 1560-TK-006 EXTERNAL COND COLLECTION TANK | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6401 | NEW | 1560-PI-6401 | VENDOR SUPPLY PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5164 | 1560-TK-006 EXTERNAL COND COLLECTION TANK | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-6401 | NEW | 1560-LS-6401 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1560-PR-PID-0000-EXP-5164 | 1560-TK-006 EXTERNAL COND COLLECTION TANK | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6403 | NEW | 1560-PI-6403 | VENDOR SUPPLY PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5164 | 1560-PP-008 EXTERNAL COND PUMP | 3"-LCD-1560-9616-CBO-- | 1560-TK-006 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6404 | NEW | 1560-PI-6404 | VENDOR SUPPLY PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5164 | 1560-PP-009 EXTERNAL COND PUMP | 3"-LCD-1560-9626-CBO-- | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9334 | NEW | 1560-PI-9334 | VENDOR SUPPLY PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5177 | ACC VACUUM PUMP INLET | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9334 | NEW | 1560-TW-9334 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | ACC HEAT EXCH INLET | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9334 | NEW | 1560-TI-9334 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | ACC HEAT EXCH INLET | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9341 | NEW | 1560-TW-9341 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | ACC HEAT EXCH OUTLET | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9341 | NEW | 1560-TI-9341 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | ACC HEAT EXCH OUTLET | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-7503 | NEW | 1560-RO-7503 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5177 | CW SUPPLY TO ACC | ------ | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8205 | NEW | 1560-PI-8205 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5177 | CW SUPPLY TO ACC | ------ | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9340 | NEW | 1560-TW-9340 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | CW RETURN FROM ACC | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9340 | NEW | 1560-TI-9340 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | CW RETURN FROM ACC | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8206 | NEW | 1560-PI-8206 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5177 | CW RETURN FROM ACC | ------ | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7413 | NEW | 1560-TW-7413 | THERMOWELL | 1560-PR-PID-0000-EXP-5177 | CONDENSATE TO GLAND SEALING SYSTEM | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7413 | NEW | 1560-TI-7413 | TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | CONDENSATE TO GLAND SEALING SYSTEM | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8207 | NEW | 1560-PI-8207 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5177 | CONDENSATE TO GLAND SEALING SYSTEM | ------ | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9351 | NEW | 1560-TW-9351 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | ACC AFTER CONDENSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9351 | NEW | 1560-TI-9351 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | ACC AFTER CONDENSER TEMPERATURE | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9350 | NEW | 1560-TW-9350 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | ACC INTER CONDENSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | 47 | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9350 | NEW | 1560-TI-9350 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | ACC INTER CONDENSER TEMPERATURE | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9347 | NEW | 1560-PI-9347 | VENDOR SUPPLY PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5177 | ACC INTER CONDENSER PRESSURE | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9362 | NEW | 1560-PSV-9362 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1560-PR-PID-0000-EXP-5177 | ACC INTER CONDENSER | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-9343 | NEW | 1560-FI-9343 | VENDOR SUPPLY FLOW GAUGE - ROTAMETER | 1560-PR-PID-0000-EXP-5177 | LOW PRESSURE STEAM FROM ACC | ------ | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9360 | NEW | 1560-PSV-9360 | VENDOR SUPPLY PRESSURE RELIEF VALVE | 1560-PR-PID-0000-EXP-5177 | LOW PRESSURE CONDENSATE FROM ACC | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6026 | NEW | 1560-PSV-6026 | PRESSURE RELIEF VALVE | 1560-PR-PID-0000-EXP-5177 | CW RETURN FROM ACC | ------ | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-6403 | NEW | 1560-HS-6403 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5164 | 1560-PP-008 EXTERNAL COND PUMP | ------ | 1560-TK-006 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-6404 | NEW | 1560-HS-6404 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5164 | 1560-PP-009 EXTERNAL COND PUMP | ------ | 1560-TK-006 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-XEV-6401 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | ------ | 1560-TK-006 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-XV-6401 | ON/OFF VALVE | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | 2"-RAW-1560-9625-CBA-- | 1560-TK-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-HS-6401 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | ------ | 1560-TK-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-ZAC-6401 | DCS INDICATION | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | ------ | 1560-TK-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-ZAO-6401 | DCS INDICATION | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | ------ | 1560-TK-006 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-ZSC-6401 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | ------ | 1560-TK-006 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-ZSO-6401 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5164 | EXTERNAL COND COLLECTION TANK INLET | ------ | 1560-TK-006 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-HS-9350 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5177 | VACUUM PUMP START | ------ | 1560-TK-006 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6401 | NEW | 1560-HS-9351 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5177 | VACUUM PUMP STOP | ------ | 1560-TK-006 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-XEV-9329 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | Vendor | DCS | DO-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-XV-9329 | VENDOR SUPPLY ON/OFF VALVE | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-XA-9329 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-ZAC-9329 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-ZAO-9329 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-ZSC-9329 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9329 | NEW | 1560-ZSO-9329 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | TR WATER HEADER TO ACC | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-XEV-9324 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | Vendor | DCS | DO-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-XV-9324 | VENDOR SUPPLY ON/OFF VALVE | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-XA-9324 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-ZAC-9324 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-ZAO-9324 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-ZSC-9324 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9324 | NEW | 1560-ZSO-9324 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9352 | NEW | 1560-HS-9352 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5177 | ACC START AIR REMOVAL SYSTEM | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9354 | NEW | 1560-HS-9354 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5177 | ACC STOP AIR REMOVAL SYSTEM | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9357 | NEW | 1560-XA-9357 | DCS ALARM | 1560-PR-PID-0000-EXP-5177 | ACC RUNNING STATUS | ------ | 1560-CD-001 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-XEV-9363 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DO-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-XV-9363 | VENDOR SUPPLY ON/OFF VALVE | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-XA-9363 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-ZAC-9363 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-ZAO-9363 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-ZSC-9363 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9363 | NEW | 1560-ZSO-9363 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-XEV-9366 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DO-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-XV-9366 | VENDOR SUPPLY ON/OFF VALVE | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-XA-9366 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | DI-S | RIO | 24V | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-ZAC-9366 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-ZAO-9366 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-ZSC-9366 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9366 | NEW | 1560-ZSO-9366 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO OUTLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-XEV-9340 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DO-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-XV-9340 | VENDOR SUPPLY ON/OFF VALVE | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-XA-9340 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | DI-S | RIO | 24V | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-ZAC-9340 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-ZAO-9340 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-ZSC-9340 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9340 | NEW | 1560-ZSO-9340 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5177 | STEAM TO INLET CONDENSOR | ------ | 1560-CD-001 | Vendor | DCS | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6016 | NEW | 1560-TW-6016 | THERMOWELL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 16"-LPS-1560-6535-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7402 | NEW | 1560-TE-7402 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6016 | NEW | 1560-TIT-6016 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6016 | NEW | 1560-TI-6016 | DCS INDICATION | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9336 | NEW | 1560-PIT-9336 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | N/A | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9336 | NEW | 1560-PIA-9336 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9336 | NEW | 1560-PY-9336 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5177 | STEAM TO ACC VACUUM PUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9352 | NEW | 1560-PIT-9352 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | N/A | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9352 | NEW | 1560-PIA-9352 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9352 | NEW | 1560-PIAH-9352 | DCS ALARM | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9352 | NEW | 1560-PIAL-9352 | DCS ALARM | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9352 | NEW | 1560-PSLL-9352 | INTLK | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9352 | NEW | 1560-PSHH-9352 | INTLK | 1560-PR-PID-0000-EXP-5177 | 150 PSIG STEAM TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9344 | NEW | 1560-PIT-9344 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5177 | STEAM FROM AIR COOLER TO ACC | ------ | N/A | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9344 | NEW | 1560-PIA-9344 | DCS INDICATION | 1560-PR-PID-0000-EXP-5177 | STEAM FROM AIR COOLER TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9344 | NEW | 1560-PY-9344 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5177 | STEAM FROM AIR COOLER TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6017 | NEW | 1560-PIT-6017 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 16"-LPS-1560-6535-CBO-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6017 | NEW | 1560-PIC-6017 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6017 | NEW | 1560-PAH-6017 | DCS ALARM | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6017 | NEW | 1560-PY-6017 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6017 | NEW | 1560-PCV-6017 | SPRAY DESUPERHEATER CONTROL VALVE | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH LETDOWN | 6"-HPS-1560-6110-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TW-6018 | THERMOWELL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TE-7403 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TIT-6018 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TIC-6018 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TAH-6018 | DCS ALARM | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TY-6018A | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TY-6018 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TCV-6018A | SPRAY DESUPERHEATER | 1560-PR-PID-0000-EXP-5160 | HP to LP LETDOWN STEAM DESH | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-TCV-6018 | SPRAY DESUPERHEATER CONTROL VALVE | 1560-PR-PID-0000-EXP-5165 | HP to LP SPRAY WATER CONTROL VALVE | 2"-BFW-1560-6115-CEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6018 | NEW | 1560-XB-6018 | VENT SILENCER | 1560-PR-PID-0000-EXP-5159 | LP STEAM TO DISTRIBUTION HEADER | 14"-HPS-1560-6106-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6018 | NEW | 1560-PY-6018 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5159 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6018 | NEW | 1560-PCV-6018 | CONTROL VALVE PART OF SILENCER | 1560-PR-PID-0000-EXP-5159 | LP STEAM TO DISTRIBUTION HEADER | 14"-HPS-1540-4190-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6019 | NEW | 1560-PIT-6019 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | 16"-LPS-1560-6113-CBO-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6019 | NEW | 1560-PIC-6019 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6019 | NEW | 1560-PAH-6019 | DCS ALARM | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6019 | NEW | 1560-PY-6019 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6019 | NEW | 1560-PCV-6019 | CONTROL VALVE PART OF SILENCER | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO DISTRIBUTION HEADER | 4"-LPS-1560-9429-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6030 | NEW | 1560-XB-6030 | VENT SILENCER | 1560-PR-PID-0000-EXP-5165 | TG SET STEAM VENT | 4"-LPS-1560-9429-CBO-FP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6235 | NEW | 1560-TW-6235 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6235 | NEW | 1560-TE-6235 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6235 | NEW | 1560-TIT-6235 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6235 | NEW | 1560-TI-6235 | TEMPERATURE INDICATOR | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6235 | NEW | 1560-TI-6235 | TEMPERATURE INDICATOR | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TW-6256 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TE-6256 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TIT-6256 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | PLC | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TIA-6256 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TIA-6256 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TISA-6256 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6256 | NEW | 1560-TISA-6256 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6257 | NEW | 1560-TW-6257 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6257 | NEW | 1560-TE-6257 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6257 | NEW | 1560-TIT-6257 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6257 | NEW | 1560-TIA-6257 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6257 | NEW | 1560-TIA-6257 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6258 | NEW | 1560-TW-6258 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6258 | NEW | 1560-TE-6258 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | 14"-HPS-1560-4190-AEA-HC- | 1560-TG-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6258 | NEW | 1560-TIT-6258 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6258 | NEW | 1560-TIA-6258 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6258 | NEW | 1560-TIA-6258 | DCS ALARM | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B TO TG | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-Z-6276 | NEW | 1560-ZI-6276 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6277 | NEW | 1560-XV-6277 | ON/OFF VALVE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | 14"-LPS-1560-563-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-Z-6277 | NEW | 1560-ZI-6277 | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-Z-6277 | NEW | 1560-ZI-6277 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6300 | NEW | 1560-PS-6300 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6300 | NEW | 1560-PS-6300 | VENDOR SUPPLY PRESSURE SWITCH | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6300 | NEW | 1560-PS-6300 | VENDOR SUPPLY PRESSURE SWITCH | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6301 | NEW | 1560-PS-6301 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6301 | NEW | 1560-PS-6301 | VENDOR SUPPLY PRESSURE SWITCH | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6301 | NEW | 1560-PS-6301 | VENDOR SUPPLY PRESSURE SWITCH | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6303 | NEW | 1560-PS-6303 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6303 | NEW | 1560-PS-6303 | VENDOR SUPPLY PRESSURE SWITCH | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6303 | NEW | 1560-PS-6303 | VENDOR SUPPLY PRESSURE SWITCH | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | DI-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PT-6316 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | 14"-LPS-1560-0563-CO-HC- | N/A | Vendor | PLC | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PICA-6316 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | ------ | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PIA-6316 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | TG EXTRACTION PORT | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PIT-6321 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | 14"-HPS-1540-4190-AEA-HC- | 1560-TG-001 | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-001 | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PIA-6321 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PIA-6321 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PICA-6321 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PICA-6321 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PIT-6322 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | 14"-HPS-1540-4190-AEA-HC- | 1560-TG-001 | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-001 | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PI-6322 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PI-6322 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PIT-6323 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | 14"-HPS-1540-4190-AEA-HC- | 1560-TG-001 | Vendor | DCS | AI-HART-S | RIO | 4-20mA HART | PECS | 1560 | N | 1560-JBP-001 | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PI-6323 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-PI-6323 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP SUPERHEATER 1B | ------ | 1560-TG-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | N
1500 | 1560 | TURBO GENERATOR | 1560-Z-6276 | NEW | 1560-ZI-6276 | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-Z-6276 | NEW | 1560-ZI-6276 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-XV-6368 | ON/OFF VALVE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | 14"-LPS-1560-563-CBO-HC- | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-XEV-6368 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | DO-S | RIO | 24V | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-ZIC-6368 | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | DI-S | PLC | 24V | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-ZIC-6368 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-ZIC-6368 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-ZIO-6369 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-ZIO-6369 | VENDOR INTERFACE | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-6368 | NEW | 1560-ZIO-6369 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5160 | LP STEAM TO DESUPERHEATER | ------ | N/A | Vendor | PLC | DI-S | PLC | 24V | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-FIT-6408 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5160 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | DCS | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-FAH-6408 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | RIO | SOFT | DCS | 1560 | N | N/A
1500 | 1560 | TURBO GENERATOR | 1560-P-6321 | NEW | 1560-FI-6408 | DCS INDICATION | 1560-PR-PID-0000-EXP-5160 | HP STEAM FROM HP SH 1B | ------ | N/A | EXP | DCS | SOFTWARE | RIO | SOFT | DCS | 1560 | N | N/A
1500 | 1560 | TURBO GENERATOR | 1560-F-6670 | NEW | 1560-FE-6670 | FLOW ELEMENT - PITOT TUBE | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6670 | NEW | 1560-FIT-6670 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6670 | NEW | 1560-FI-6670 | DCS INDICATION | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6675 | NEW | 1560-FE-6675 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | 4"-BFW-1560-6102-CEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6675 | NEW | 1560-FIT-6675 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6675 | NEW | 1560-FI-6675 | DCS INDICATION | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6671 | NEW | 1560-TW-6671 | THERMOWELL | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7404 | NEW | 1560-TE-7404 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6671 | NEW | 1560-TIT-6671 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6671 | NEW | 1560-TI-6671 | DCS INDICATION | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6671 | NEW | 1560-TAL-6671 | DCS ALARM | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-PIT-6672 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | 24"-HPS-1560-6104-AEA-HC- | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-PIC-6672 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-PI-6672 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-PY-6672 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-PCV-6672 | SPRAY DESUPERHEATER CONTROL VALVE | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS VALVE | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-ZIT-6672 | POSITION TRANSMITTER | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS VALVE | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | DCS | AI | DCS | 4-20mA | FLD-INLINE | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-6672 | NEW | 1560-ZI-6672 | DCS INDICATION | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS VALVE | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | DCS | DCS | DCS | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6673 | NEW | 1560-TW-6673 | THERMOWELL | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | 24"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8801 | NEW | 1570-TE-8801 | TEMPERATURE ELEMENT - TC TYPE K | 1570-PR-PID-0000-EXP-5188 | ACID RECIRC PUMPS SUCTION | 8"-ACC-1570-7121-SBQ-FP-ET | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6673 | NEW | 1560-TIT-6673 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6673 | NEW | 1560-TI-6673 | DCS INDICATION | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6673 | NEW | 1560-TAH-6673 | DCS ALARM | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6673 | NEW | 1560-TAL-6673 | DCS ALARM | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6674 | NEW | 1560-TW-6674 | THERMOWELL | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | 4"-BFW-1560-6102-CEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8820 | NEW | 1570-TE-8820 | TEMPERATURE ELEMENT - TC TYPE K | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | 4"-ACC-1570-8803-SBQ-FP-ET | 1570-ZE-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6674 | NEW | 1560-TIT-6674 | TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6674 | NEW | 1560-TI-6674 | DCS INDICATION | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6674 | NEW | 1560-TY-6674 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS SPRAY WATER VALVE | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6674 | NEW | 1560-TCV-6674 | SPRAY DESUPERHEATER CONTROL VALVE | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS SPRAY WATER VALVE | 4"-BFW-1560-6102-CEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-6670 | NEW | 1560-UY-6670 | DCS CALCULATION | 1560-PR-PID-0000-EXP-5166 | HP STEAM TO SPRAY DESH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6677 | NEW | 1560-TY-6677 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS DESH | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6677 | NEW | 1560-TCV-6677 | SPRAY DESUPERHEATER | 1560-PR-PID-0000-EXP-5166 | HP STG BYPASS DESH | 14"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-7400 | NEW | 1560-RO-7400 | VENDOR SUPPLY ORIFICE PLATE | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-HC- | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7401 | NEW | 1560-TW-7401 | THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7401 | NEW | 1560-TE-7401 | TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | DCS | E-T | N/A | E-T | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7401 | NEW | 1560-TI-7401 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7414 | NEW | 1560-TIA-7414 | TEMPERATURE INDICATOR | 1560-PR-PID-0000-EXP-5174 | ACC COND TEMP |  | NA | EXP | NA | NA | NA | NA | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7415 | NEW | 1560-TIA-7415 | TEMPERATURE INDICATOR | 1560-PR-PID-0000-EXP-5174 | ACC COND TEMP |  | NA | EXP | NA | NA | NA | NA | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7416 | NEW | 1560-TIA-7416 | TEMPERATURE INDICATOR | 1560-PR-PID-0000-EXP-5174 | AMBIENT TEMP |  | NA | EXP | NA | NA | NA | NA | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7402 | NEW | 1560-TW-7402 | THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8821 | NEW | 1570-TE-8821 | TEMPERATURE ELEMENT - TC TYPE K | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | 4"-ACC-1570-8804-SBQ-FP-ET | 1570-ZE-004 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7402 | NEW | 1560-TI-7402 | TEMPERATURE INDICATOR | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7403 | NEW | 1560-VE-7403 | VIBRATION ELEMENT | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 1 | ------ | 1560-CD-001 | EXP | DCS | DCS | DCS | N/A | FLD-EQUIP | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7403 | NEW | 1560-VT-7403 | VIBRATION TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 1 | ------ | 1560-CD-001 | EXP | DCS | AI-HART | DCS | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7403 | NEW | 1560-VI-7403 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 1 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TW-7403 | THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-9200 | NEW | 1570-TE-9200 | TEMPERATURE ELEMENT - TC TYPE K | 1570-PR-PID-0000-EXP-5192 | ACID TRUCKS LOADING ARMS HEADER | 10"-ACC-1570-7106-SBQ-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TI-7403 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7404 | NEW | 1560-VE-7404 | VIBRATION ELEMENT | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 2 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7404 | NEW | 1560-VI-7404 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 2 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7404 | NEW | 1560-VT-7404 | VIBRATION TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 2 | ------ | 1560-CD-001 | EXP | DCS | AI-HART | DCS | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7404 | NEW | 1560-TW-7404 | THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | 120"-LPS-1560-6118-CS-- | 1560-CD-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-7247 | NEW | 1540-TE-7247 | TEMPERATURE ELEMENT - TC TYPE K | 1540-PR-PID-0000-EXP-5072 | HP STEAM FROM HP SH 4A | 12"-HPS-1540-9434-AEA-HC- | 1540-HX-004 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1540 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7404 | NEW | 1560-TI-7404 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC LOW PRESS STEAM INLET | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7405 | NEW | 1560-VE-7405 | VIBRATION ELEMENT | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 3 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7405 | NEW | 1560-VI-7405 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 3 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-V-7405 | NEW | 1560-VT-7405 | VIBRATION TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 3 | ------ | 1560-CD-001 | EXP | DCS | AI-HART | DCS | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7405 | NEW | 1560-LIA-7405 | LEVEL INDICATOR - LOCAL | 1560-PR-PID-0000-EXP-5174 | DRAIN POT LEVEL CONTROL | ------ | NA | EXP | DCS | N/A | RIO | N/A | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7405 | NEW | 1560-LT-7405 | LEVEL TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5174 | DRAIN POT LEVEL CONTROL | ------ | NA | EXP | N/A | N/A | N/A | N/A | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7406 | NEW | 1560-LIA-7406 | LEVEL INDICATOR - LOCAL | 1560-PR-PID-0000-EXP-5174 | DRAIN POT LEVEL CONTROL |  | NA | EXP | N/A | N/A | RIO | N/A | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7406 | NEW | 1560-LT-7406 | LEVEL TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5174 | DRAIN POT LEVEL CONTROL |  | NA | EXP | N/A | N/A | N/A | N/A | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7407 | NEW | 1560-LICA-7407 | LEVEL INDICATOR - LOCAL | 1560-PR-PID-0000-EXP-5174 | DRAIN POT LEVEL CONTROL |  | NA | EXP | DCS | AI-HART S | RIO | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7407 | NEW | 1560-LT-7407 | LEVEL TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5174 | DRAIN POT LEVEL CONTROL |  | NA | EXP | N/A | N/A | N/A | N/A | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7407 | NEW | 1560-HS-7407 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 1 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7407 | NEW | 1560-PIC-7407 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 1 | ------ | 1560-CD-001 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7408 | NEW | 1560-HS-7408 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 2 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7408 | NEW | 1560-PIC-7408 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 2 | ------ | 1560-CD-001 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7409 | NEW | 1560-HS-7409 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 3 | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7409 | NEW | 1560-PIC-7409 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC FAN MOTOR 3 | ------ | 1560-CD-001 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9407 | NEW | 1560-LSHH-9407 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC DRAIN POT | ------ | 1560-CD-001 | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9408 | NEW | 1560-LSH-9408 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC DRAIN POT | ------ | 1560-CD-001 | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9408 | NEW | 1560-LSH-9408 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1560-PR-PID-0000-EXP-5174 | ACC DRAIN POT | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9407 | NEW | 1560-LSHH-9407 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1560-PR-PID-0000-EXP-5174 | ACC DRAIN POT | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7441 | NEW | 1540-AE-7441 | SO2 AREA MONITOR SENSOR | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1540-PV-003 | EXP | N/A | E-T | N/A | mV | FLD-OFFLINE | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7441 | NEW | 1540-AIT-7441 | SO2 AREA MONITOR | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7441 | NEW | 1540-AI-7441 | DCS INDICATION | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7441 | NEW | 1540-AAH-7441 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7441 | NEW | 1540-AAHH-7441 | DCS ALARM | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-A-7441 | NEW | 1540-ASH-7441 | INTLK | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1540-PV-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7441 | NEW | 1540-XA-7441A | ALARM BEACON | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1560-CD-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7441 | NEW | 1540-XA-7441B | ALARM HORN | 1540-PR-PID-0000-EXP-5074 | 1540-PV-003 STEAM DRUM | ------ | 1560-CD-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7441 | NEW | 1560-AE-7441 | SO2 AREA MONITOR SENSOR | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | N/A | E-T | N/A | mV | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7441 | NEW | 1560-AIT-7441 | SO2 AREA MONITOR | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7441 | NEW | 1560-AI-7441 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7441 | NEW | 1560-AAH-7441 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7441 | NEW | 1560-AAHH-7441 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7441 | NEW | 1560-ASH-7441 | INTLK | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7241 | NEW | 1540-XA-7241A | ALARM BEACON | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7241 | NEW | 1540-XA-7241B | ALARM HORN | 1540-PR-PID-0000-EXP-5072 | ECON | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7441 | NEW | 1560-XA-7441A | ALARM BEACON | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7441 | NEW | 1560-XA-7441B | ALARM HORN | 1560-PR-PID-0000-EXP-5174 | 1560-CD-001 ACC | ------ | 1560-CD-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7501 | NEW | 1560-LT-7501 | LEVEL TRANSMITTER - GWR | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7502 | NEW | 1560-LT-7502 | LEVEL TRANSMITTER - GWR | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7520 | NEW | 1560-PI-7520 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMP | 4"-LCD-1560-7402-CBO-HC-ET | 1560-PP-019 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-7521 | NEW | 1560-PI-7521 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMP | 4"-BFW-1560-6102-CEA-HC-ET | 1560-PP-019 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-7522 | NEW | 1560-PI-7522 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMP | 4"-LCD-1560-7404-CBO-HC-ET | 1560-PP-020 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-7523 | NEW | 1560-PI-7523 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMP | 4"-BFW-1560-7405-CEA-HC-ET | 1560-PP-020 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-H-7518 | NEW | 1560-HS-7518 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMP TO OFF-SPEC COND. | ------ | 1560-PP-020 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7519 | NEW | 1560-HS-7519 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMP | ------ | 1560-PP-019 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7524 | NEW | 1560-PIT-7524 | PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. TO HP TG BYPASS SH | 4"-BFW-1560-6102-CEA-HC-ET | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | YES
1500 | 1560 | TURBO GENERATOR | 1560-P-7524 | NEW | 1560-PIC-7524 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. TO HP TG BYPASS SH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7524 | NEW | 1560-PAL-7524 | DCS ALARM | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. TO HP TG BYPASS SH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7524 | NEW | 1560-PSLL-7524 | INTLK | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. TO HP TG BYPASS SH | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7524 | NEW | 1560-PY-7524 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. TO HP TG BYPASS SH | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7524 | NEW | 1560-PCV-7524 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. TO HP TG BYPASS SH | 4"-BFW-1560-6102-CEA-HC-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-L-7507 | NEW | 1560-LIT-7507 | LEVEL TRANSMITTER - GWR | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7507 | NEW | 1560-LIC-7507 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7507 | NEW | 1560-LSLL-7507 | INTLK | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7507 | NEW | 1560-LY-7507 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-7507 | NEW | 1560-LCV-7507 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5175 | COND. TK | 8"-LCD-1560-6123-CBO-HC- | 1560-TK-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LY-9320 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LCV-9320 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5175 | COND. TK | 2"-TRW-1560-9623-SBA-FP-ET | 1560-TK-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-HS-9320 | OPERATOR INITIATED DCS SELECTOR | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LAL-9320 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LAH-9320 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LSHH-9320 | INTLK | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LSH-9320 | INTLK | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LSLL-9320 | INTLK | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LIA-9320 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5175 | COND. TK | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7511 | NEW | 1560-FE-7511 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | 8"-LCD-1560-6123-CBO-HC- | 1560-TK-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7511 | NEW | 1560-FIT-7511 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | ------ | 1560-TK-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7511 | NEW | 1560-FIC-7511 | DCS INDICATION AND CONTROL | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7511 | NEW | 1560-FSLL-7511 | INTLK | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | ------ | 1560-TK-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7511 | NEW | 1560-FY-7511 | SMART VALVE POSITIONER | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | ------ | 1560-TK-004 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7511 | NEW | 1560-FCV-7511 | CONTROL VALVE | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | 4"-LCD-1560-7403-CBO-HC-ET | 1560-TK-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | YES
1500 | 1560 | TURBO GENERATOR | 1560-T-7510 | NEW | 1560-TW-7510 | THERMOWELL | 1560-PR-PID-0000-EXP-5175 | ACC COND. TO BFW PREHEATER | 8"-LCD-1560-9537-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7510 | NEW | 1560-TI-7510 | TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5175 | ACC COND. TO BFW PREHEATER | 8"-LCD-1560-9537-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7527 | NEW | 1560-TW-7527 | THERMOWELL | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | 8"-LCD-1560-6123-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7527 | NEW | 1560-TI-7527 | TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5176 | ACC COND. RECYCLE | 8"-LCD-1560-6123-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9325 | NEW | 1560-TI-9325 | DCS INDICATION | 1560-PR-PID-0000-EXP-5175 | COND. TANK TEMPERATURE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9325 | NEW | 1560-TAL-9325 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | COND. TANK TEMPERATURE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9325 | NEW | 1560-TIT-9325 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5175 | COND. TANK TEMPERATURE | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9323 | NEW | 1560-PIT-9323 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5175 | COND. TANK PRESSURE | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9320 | NEW | 1560-LIT-9320 | VENDOR SUPPLY D/P LEVEL TRANSMITTER | 1560-PR-PID-0000-EXP-5175 | COND. TANK TEMPERATURE | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9321 | NEW | 1560-LIT-9321 | VENDOR SUPPLY D/P LEVEL TRANSMITTER | 1560-PR-PID-0000-EXP-5175 | COND. TANK TEMPERATURE | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9322 | NEW | 1560-LIT-9322 | VENDOR SUPPLY D/P LEVEL TRANSMITTER | 1560-PR-PID-0000-EXP-5175 | COND. TANK TEMPERATURE | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9323 | NEW | 1560-PSH-9323 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | COND. TANK PRESSURE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9323 | NEW | 1560-PSHH-9323 | INTLK | 1560-PR-PID-0000-EXP-5175 | COND. TANK PRESSURE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9323 | NEW | 1560-PIA-9323 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | COND. TANK PRESSURE | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7516 | NEW | 1560-HS-7516 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5175 | ACC COND. TRANSFER PUMP | ------ | 1560-PP-015 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-7517 | NEW | 1560-HS-7517 | MOTOR CONTROL | 1560-PR-PID-0000-EXP-5175 | ACC COND. TRANSFER PUMP | ------ | 1560-PP-016 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1560 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7508 | NEW | 1560-PI-7508 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5175 | ACC COND. TRANSFER PUMP DISCH | 8"-LCD-1560-9537-CBO-HC- | 1560-PP-015 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-7509 | NEW | 1560-PI-7509 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5175 | ACC COND. TRANSFER PUMP DISCH | 8"-LCD-1560-6124-CBO-HC- | 1560-PP-016 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7512 | NEW | 1560-AE-7512 | ANALYZER SENSOR - CONDUCTIVITY | 1560-PR-PID-0000-EXP-5176 | ACC COND. TRANSFER | 8"-LCD-1560-6123-CBO-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7512 | NEW | 1560-AIT-7512 | ANALYZER TRANSMITTER - CONDUCTIVITY | 1560-PR-PID-0000-EXP-5176 | ACC COND. TRANSFER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7512 | NEW | 1560-AI-7512 | DCS INDICATION | 1560-PR-PID-0000-EXP-5176 | ACC COND. TRANSFER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7512 | NEW | 1560-AAL-7512 | DCS ALARM | 1560-PR-PID-0000-EXP-5176 | ACC COND. TRANSFER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7512 | NEW | 1560-AAH-7512 | DCS ALARM | 1560-PR-PID-0000-EXP-5176 | ACC COND. TRANSFER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7512 | NEW | 1560-ASHH-7512 | INTLK | 1560-PR-PID-0000-EXP-5176 | ACC COND. TRANSFER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7513 | NEW | 1560-XEV-7513 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5176 | OFF SPEC ACC COND. | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7513 | NEW | 1560-XV-7513 | ON/OFF VALVE | 1560-PR-PID-0000-EXP-5176 | OFF SPEC ACC COND. | 8"-LCD-1560-6125-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7513 | NEW | 1560-ZAC-7513 | DCS INDICATION | 1560-PR-PID-0000-EXP-5176 | OFF SPEC ACC COND. | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7513 | NEW | 1560-ZAO-7513 | DCS INDICATION | 1560-PR-PID-0000-EXP-5176 | OFF SPEC ACC COND. | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7513 | NEW | 1560-ZSC-7513 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5176 | OFF SPEC ACC COND. | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7513 | NEW | 1560-ZSO-7513 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5176 | OFF SPEC ACC COND. | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7514 | NEW | 1560-XEV-7514 | PART OF VALVE SOLENOID VALVE | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7514 | NEW | 1560-XV-7514 | ON/OFF VALVE | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | 8"-LCD-1560-6123-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7514 | NEW | 1560-ZAC-7514 | DCS INDICATION | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7514 | NEW | 1560-ZAO-7514 | DCS INDICATION | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7514 | NEW | 1560-ZSC-7514 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7514 | NEW | 1560-ZSO-7514 | PART OF VALVE LIMIT SWITCH | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-7510 | NEW | 1560-RO-7510 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5176 | BYPASS COND. PUMPS RECYCLE | 1"-BFW-1560-5129-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-7527 | NEW | 1560-RO-7527 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5160 | TG EXTERNAL COND TANK | 3/4"-HCD-1560-9624-AEA-PP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-7529 | NEW | 1560-RO-7529 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5160 | TG EXTERNAL COND TANK | 3/4"-HCD-1560-0441-AEA-PP- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-R-7509 | NEW | 1560-RO-7509 | RESTRICTION ORIFICE | 1560-PR-PID-0000-EXP-5175 | ACC COND. PUMPS RECYCLE | 1"-LCD-1560-6127-CBA-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7541 | NEW | 1560-AE-7541 | SO2 AREA MONITOR SENSOR | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | N/A | E-T | N/A | mV | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-3641 | NEW | 1560-AIT-3641 | SO2 AREA MONITOR | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP |  | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-3641 | NEW | 1560-AE-3641 | SO2 AREA MONITOR SENSOR | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | N/A | E-T | N/A | mV | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-3641 | NEW | 1560-AI-3641 | DCS INDICATION | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-3641 | NEW | 1560-AH-3641 | DCS ALARM | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-3641 | NEW | 1560-AAH-3641 | DCS ALARM | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-3641 | NEW | 1560-ASH-3641 | INTLK | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7541 | NEW | 1560-AIT-7541 | SO2 AREA MONITOR | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | AI-HART | DCS | 4-20mA HART | DCS | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7541 | NEW | 1560-AI-7541 | DCS INDICATION | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7541 | NEW | 1560-AAH-7541 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7541 | NEW | 1560-AAHH-7541 | DCS ALARM | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-A-7541 | NEW | 1560-ASH-7541 | INTLK | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-3641 | NEW | 1560-XA-3641A | ALARM BEACON | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-3641 | NEW | 1560-XA-3641B | ALARM HORN | 1560-PR-PID-0000-EXP-5136 | WT AREA SUMP | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7541 | NEW | 1560-XA-7541A | ALARM BEACON | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-7541 | NEW | 1560-XA-7541B | ALARM HORN | 1560-PR-PID-0000-EXP-5175 | 1560-TK-004 COND TANK | ------ | 1560-CD-001 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1560 | N | 1560-JBP-001 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7526 | NEW | 1560-FE-7526 | FLOW ELEMENT - ORIFICE PLATE | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | 8"-LCD-1560-6123-CBO-HC- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7526 | NEW | 1560-FIT-7526 | FLOW TRANSMITTER - D/P | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-002 | NO
1500 | 1560 | TURBO GENERATOR | 1560-F-7526 | NEW | 1560-FI-7526 | DCS INDICATION | 1560-PR-PID-0000-EXP-5176 | ACC COND. TO BFW PREHEATER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8202 | NEW | 1560-PI-8202 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5182 | IP AUX BOILER CW SUPPLY | 1"-CLW-1560-9464-CBA-FP- | 1560-BO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8204 | NEW | 1560-PI-8204 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5182 | IP AUX BOILER CW RETURN | 1"-CLW-1560-6749-CBA-FP- | 1560-BO-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8610 | NEW | 1570-HS-8610 | DCS OPERATOR INITIATED CONTROL | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1570-TK-001 | EXP | DCS | DCS | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8610 | NEW | 1570-XEV-8610 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1570-TK-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8610 | NEW | 1570-XV-8610 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | 10"-ACC-1570-9414-SBQ-- | 1570-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8610 | NEW | 1570-ZSC-8610 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8610 | NEW | 1570-ZAC-8610 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8610 | NEW | 1570-ZSO-8610 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8610 | NEW | 1570-ZAO-8610 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8604 | NEW | 1570-HS-8604 | DCS SELECTOR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | DCS | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8601 | NEW | 1570-HS-8601 | DCS SELECTOR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8611 | NEW | 1570-HS-8611 | DCS OPERATOR INITIATED CONTROL | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1570-TK-002 | EXP | DCS | DCS | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8611 | NEW | 1570-XEV-8611 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1570-TK-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8611 | NEW | 1570-XV-8611 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | 10"-ACC-1570-7109-SBQ-- | 1570-TK-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8611 | NEW | 1570-ZSC-8611 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8611 | NEW | 1570-ZAC-8611 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8611 | NEW | 1570-ZSO-8611 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-8611 | NEW | 1570-ZAO-8611 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK OUTLET | ------ | 1520-TW-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8615 | NEW | 1570-FE-8615 | FLOW ELEMENT - MAGNETIC | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH RECIRC | 6"-ACC-1570-7104-SBQ-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8615 | NEW | 1570-FIT-8615 | FLOW TRANSMITTER - MAGNETIC | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH RECIRC | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8615 | NEW | 1570-FIC-8615 | DCS INDICATION AND CONTROL | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH RECIRC | ------ | N/A | EXP | DCS | DCS | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8615 | NEW | 1570-FAL-8615 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH RECIRC | ------ | N/A | EXP | DCS | DCS | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8615 | NEW | 1570-FY-8615 | SMART VALVE POSITIONER | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH RECIRC | ------ | N/A | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8615 | NEW | 1570-FCV-8615 | STRONG ACID CONTROL VALVE | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH RECIRC | 3"-ACC-1570-7128-SBQ-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FE-8631 | FLOW ELEMENT - MAGNETIC | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | 6"-ACC-1570-7104-SBQ-- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FIT-8631 | FLOW TRANSMITTER - MAGNETIC | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FI-8631 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FIC-8631 | DCS INDICATION AND CONTROL | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | AI-HART-S | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FAH-8631 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FAL-8631 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8601 | NEW | 1570-FI-8601 | FLOW GAUGE - ROTAMETER | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8601 | NEW | 1570-LIT-8601 | LEVEL TRANSMITTER - RADAR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8601 | NEW | 1570-LI-8601 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8601 | NEW | 1570-LAL-8601 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8601 | NEW | 1570-LAH-8601 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8601 | NEW | 1570-LSHH-8601 | INTLK | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-R-8601 | NEW | 1570-RO-8601 | STRONG ACID ORIFICE PLATE | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | 3"-ACC-1570-7129-SBQ-- | 1570-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-EQUIP | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8604 | NEW | 1570-FI-8604 | FLOW GAUGE - ROTAMETER | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8604 | NEW | 1570-LIT-8604 | LEVEL TRANSMITTER - RADAR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8604 | NEW | 1570-LI-8604 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8604 | NEW | 1570-LAL-8604 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8604 | NEW | 1570-LAH-8604 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8604 | NEW | 1570-LSHH-8604 | INTLK | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8602 | NEW | 1570-LIT-8602 | LEVEL TRANSMITTER - GWR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8602 | NEW | 1570-LI-8602 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8602 | NEW | 1570-LAL-8602 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8602 | NEW | 1570-LAH-8602 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8605 | NEW | 1570-LIT-8605 | LEVEL TRANSMITTER - GWR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8605 | NEW | 1570-LI-8605 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8605 | NEW | 1570-LAL-8605 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8605 | NEW | 1570-LAH-8605 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR TK | ------ | 1570-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8603 | NEW | 1570-LIT-8603 | LEVEL TRANSMITTER - RADAR | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR SUMP | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8603 | NEW | 1570-LI-8603 | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-8603 | NEW | 1570-LAH-8603 | DCS ALARM | 1570-PR-PID-0000-EXP-5186 | PROD ACID STOR SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8619 | NEW | 1570-HS-8619A | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP | ------ | 1570-PP-001 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8619 | NEW | 1570-JI-8619A | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | PROD ACID TRANSFER PUMP POWER MONITOR | ------ | 1570-PP-001 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8619 | NEW | 1570-JI-8620A | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | ACID OUJTLOADING PUMP POWER MONITOR | ------ | 1570-PP-003 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8620 | NEW | 1570-JI-8620B | DCS INDICATION | 1570-PR-PID-0000-EXP-5186 | ACID OUJTLOADING PUMP POWER MONITOR | ------ | 1570-PP-004 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8620 | NEW | 1570-JI-8619B | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | PROD ACID TRANSFER PUMP POWER MONITOR | ------ | 1570-PP-002 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8619 | NEW | 1570-HS-8619B | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP | ------ | 1570-PP-002 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8620 | NEW | 1570-HS-8620A | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5186 | ACID OUJTLOADING PUMP | ------ | 1570-PP-003 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8620 | NEW | 1570-HS-8620B | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5186 | ACID OUJTLOADING PUMP | ------ | 1570-PP-004 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8209 | NEW | 1560-PI-8209 | DCS SELECTOR | 1560-PR-PID-0000-EXP-5174 | TG EXHAUST TO ACC | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8209 | NEW | 1570-PI-8209 | PRESSURE GAUGE | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | 1570-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8606 | NEW | 1570-PI-8606 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH | 6"-ACC-1570-7104-SBQ-- | 1570-PP-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8607 | NEW | 1570-PI-8607 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1570-PR-PID-0000-EXP-5186 | PROD ACID TRANSFER PUMP DISCH | 6"-ACC-1570-7105-SBQ-- | 1570-PP-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8617 | NEW | 1570-PI-8617 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1570-PR-PID-0000-EXP-5186 | ACID OUTLOADING PUMPS DISCH | 10"-ACC-1570-7106-SBQ-- | 1570-PP-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8618 | NEW | 1570-PI-8618 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1570-PR-PID-0000-EXP-5186 | ACID OUTLOADING PUMPS DISCH | 10"-ACC-1570-9417-SBQ-- | 1570-PP-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8631 | NEW | 1570-FCV-8631 | DELTED CONTROL VALVE | 1570-PR-PID-0000-EXP-5186 | PROD ACID TO LITHIUM PROCESSING | ------ | N/A | EXP | DCS | DCS | DCS | NA | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8801 | NEW | 1570-TW-8801 | THERMOWELL | 1570-PR-PID-0000-EXP-5188 | ACID RECIRC PUMPS SUCTION | 8"-ACC-1570-7121-SBQ-FP-ET | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-8208 | NEW | 1560-PI-8208 | PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5162 | GLAND STEAM CONDENSER | 8"-LCD-1560-6123-CBO-HC- | N/A | EXP | DCS | N/A | N/A | N/A | N/A | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6426 | NEW | 1560-TI-6426 | DCS INDICATION | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | ------ | N/A | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6426 | NEW | 1560-TE-6426 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5162 | HP STEAM HEADER | 2"-HPS-1560-6015-AEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8801 | NEW | 1570-TIT-8801 | TEMPERATURE INDICATING TRANSMITTER | 1570-PR-PID-0000-EXP-5188 | ACID RECIRC PUMPS SUCTION | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8801 | NEW | 1570-TI-8801 | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | ACID RECIRC PUMPS SUCTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8801 | NEW | 1570-TAL-8801 | DCS ALARM | 1570-PR-PID-0000-EXP-5188 | ACID RECIRC PUMPS SUCTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8801 | NEW | 1570-TAH-8801 | DCS ALARM | 1570-PR-PID-0000-EXP-5188 | ACID RECIRC PUMPS SUCTION | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8850A | NEW | 1570-HS-8850A | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5188 | 98.5 ACID RECIRC PUMP | ------ | 1570-PP-005 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-J-8850A | NEW | 1570-JI-8850A | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | 98.5 ACID RECIRC PUMP | ------ | 1570-PP-005 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-J-8850B | NEW | 1570-JI-8850B | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | 98.5 ACID RECIRC PUMP | ------ | 1570-PP-005 | EXP | DCS | AI | DCS | 4-20mA | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-8850B | NEW | 1570-HS-8850B | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5188 | 98.5 ACID RECIRC PUMP (STANDBY) | ------ | 1570-PP-006 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8804 | NEW | 1570-PI-8804 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1570-PR-PID-0000-EXP-5188 | 98.5 ACID RECIRC PUMP | 4"-ACC-1570-7111-SBQ-FP-ET | 1570-PP-005 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-P-8805 | NEW | 1570-PI-8805 | PRESSURE GAUGE - DIAPHRAGM SEAL | 1570-PR-PID-0000-EXP-5188 | 98.5 ACID RECIRC PUMP | 4"-ACC-1570-7112-SBQ-FP-ET | 1570-PP-006 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-TW-8806A | VENDOR SUPPLY THERMOWELL | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | 4"-ACC-1570-7111-SBQ-FP-ET | 1570-ZE-003 | Vendor | N/A | N/A | N/A | N/A | PECS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-TE-8806A | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | 4"-ACC-1570-7111-SBQ-FP-ET | 1570-ZE-003 | Vendor | N/A | E-T | N/A | mV | PECS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-TIT-8806A | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | ------ | 1570-ZE-003 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-TI-8806A | DCS Indication and Control | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | PECS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-TSH-8806A | INTLK | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-TSL-8806A | DCS ALARM | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TIT-9397 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TIA-9397 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TAH-9397 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TSHH-9397 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9402 | NEW | 1560-TIT-9402 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9402 | NEW | 1560-TIA-9402 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9402 | NEW | 1560-TAH-9402 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9402 | NEW | 1560-TSHH-9402 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9403 | NEW | 1560-TIT-9403 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9403 | NEW | 1560-TIA-9403 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9403 | NEW | 1560-TAH-9403 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9403 | NEW | 1560-TSHH-9403 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9404 | NEW | 1560-TIT-9404 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9404 | NEW | 1560-TIA-9404 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9404 | NEW | 1560-TAH-9404 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9404 | NEW | 1560-TSHH-9404 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9357 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9357 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9357 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9362 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9362 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9362 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9367 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9367 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9367 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9372 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9372 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9372 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9377 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9377 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9377 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VT-9382 | VENDOR SUPPLY VIBRATION SWITCH | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VIA-9382 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VAAH-9382 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VSHH-9382 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TIT-9398 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TIA-9398 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TAH-9398 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TSHH-9398 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9358 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9358 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9358 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9363 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9363 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9363 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9368 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9368 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9368 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9373 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9373 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9373 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9378 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9378 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9378 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VT-9383 | VENDOR SUPPLY VIBRATION SWITCH | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VIA-9383 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VAAH-9383 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VSHH-9383 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TIT-9399 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TIA-9399 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TAH-9399 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9397 | NEW | 1560-TSHH-9399 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC GEAR BOX TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9359 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9359 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9359 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9364 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9364 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9364 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9369 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9369 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9369 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9374 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9374 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9374 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIT-9379 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TIA-9379 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-TSHH-9379 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VT-9384 | VENDOR SUPPLY VIBRATION SWITCH | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VIA-9384 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VAAH-9384 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-7403 | NEW | 1560-VSHH-9384 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC MOTOR VIBRATION | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9316 | NEW | 1560-TW-9316 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9316 | NEW | 1560-TI-9316 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9317 | NEW | 1560-TW-9317 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9317 | NEW | 1560-TI-9317 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9311 | NEW | 1560-TW-9311 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9311 | NEW | 1560-TE-9311 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9311 | NEW | 1560-TIT-9311 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9311 | NEW | 1560-TIA-9311 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9312 | NEW | 1560-TIA-9312 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9312 | NEW | 1560-TSHH-9312 | DCS ALARM | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9309 | NEW | 1560-TW-9309 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9309 | NEW | 1560-TE-9309 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9309 | NEW | 1560-TIT-9309 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9309 | NEW | 1560-TIA-9309 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9310 | NEW | 1560-TW-9310 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9310 | NEW | 1560-TE-9310 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9310 | NEW | 1560-TIT-9310 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9310 | NEW | 1560-TIA-9310 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9301 | NEW | 1560-PIT-9301 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9301 | NEW | 1560-PIA-9301 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9302 | NEW | 1560-PIT-9302 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9302 | NEW | 1560-PIA-9302 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9303 | NEW | 1560-PIT-9303 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9303 | NEW | 1560-PIA-9303 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9304 | NEW | 1560-PIA-9304 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9303 | NEW | 1560-PSL-9303 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9303 | NEW | 1560-PSHH-9303 | DCS INDICATION | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9304 | NEW | 1560-PSL-9304 | INTLK | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9304 | NEW | 1560-PSHH-9304 | INTLK | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9304 | NEW | 1560-HS-9304 | OPERATOR INITIATED DCS SELECTOR | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | FLD-OFFLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-P-9308 | NEW | 1560-PI-9308 | VENDOR SUPPLY PRESSURE GAUGE | 1560-PR-PID-0000-EXP-5174 | ACC DIFUSER PRESSURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9326 | NEW | 1560-TW-9326 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9326 | NEW | 1560-TE-9326 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9326 | NEW | 1560-TIT-9326 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9326 | NEW | 1560-TIA-9326 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9326 | NEW | 1560-TSL-9326 | INTLK | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TW-9328 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TE-9328 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TIT-9328 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TIA-9328 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TSL-9328 | INTLK | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TE-9300 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC AMBIENT AIR TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TIT-9300 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC AMBIENT AIR TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART | PLC | 4-20mA HART | FLD-OFFLINE | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TIA-9300 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC AMBIENT AIR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9328 | NEW | 1560-TSL-9300 | INTLK | 1560-PR-PID-0000-EXP-5174 | ACC AMBIENT AIR TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9330 | NEW | 1560-TW-9330 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9330 | NEW | 1560-TE-9330 | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | N/A | E-T | N/A | mV | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9330 | NEW | 1560-TIT-9330 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | Vendor | DCS | AI-HART-S | PLC | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9330 | NEW | 1560-TIA-9330 | DCS CONTROL FUNCTION | 1560-PR-PID-0000-EXP-5174 | ACC TEMPERATURE | ------ | 1560-CD-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9332 | NEW | 1560-HS-9332 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC START UP PERMISSIVE | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9333 | NEW | 1560-HS-9333 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC START UP | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9333 | NEW | 1560-LSHH-9333 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1560-PR-PID-0000-EXP-5177 | ACC LEVEL | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9334 | NEW | 1560-LSLL-9334 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1560-PR-PID-0000-EXP-5177 | ACC LEVEL | ------ | N/A | Vendor | DCS | AI-HART-S | DCS | 4-20mA HART | PECS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9333 | NEW | 1560-LSHH-9333 | INTLK | 1560-PR-PID-0000-EXP-5177 | ACC LEVEL | ------ | N/A | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-L-9334 | NEW | 1560-LSLL-9334 | INTLK | 1560-PR-PID-0000-EXP-5177 | ACC LEVEL | ------ | N/A | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9354 | NEW | 1560-TW-9354 | VENDOR SUPPLY THERMOWELL | 1560-PR-PID-0000-EXP-5177 | STEAM FROM AIR COOLER TO ACC | ------ | 1560-CD-001 | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-9354 | NEW | 1560-TI-9354 | VENDOR SUPPLY TEMPERATURE GAUGE | 1560-PR-PID-0000-EXP-5177 | STEAM FROM AIR COOLER TO ACC | ------ | N/A | Vendor | N/A | N/A | N/A | N/A | PECS | 1560 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-X-9334 | NEW | 1560-XA-9334 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC SHUTDOWN | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9335 | NEW | 1560-HS-9335 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC AUTO/MANUAL/LOCAL | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1560 | TURBO GENERATOR | 1560-H-9331 | NEW | 1560-HS-9331 | DCS OPERATOR INITIATED CONTROL | 1560-PR-PID-0000-EXP-5174 | ACC HEAT TRACING | ------ | 1560-CD-001 | EXP | DCS | DO-S | RIO | 24V | DCS | 1560 | N | 1560-JBP-003 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806A | NEW | 1570-HS-8806A | VENDOR INTERFACE | 1570-PR-PID-0000-EXP-5188 | ACID HEATER SA INLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-TW-8806B | VENDOR SUPPLY THERMOWELL | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | 4"-ACC-1570-7112-SBQ-FP-ET | 1570-ZE-004 | Vendor | N/A | N/A | N/A | N/A | PECS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-TE-8806B | VENDOR SUPPLY TEMPERATURE ELEMENT - TC | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | 4"-ACC-1570-7112-SBQ-FP-ET | 1570-ZE-004 | Vendor | N/A | E-T | N/A | mV | PECS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-TIT-8806B | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | ------ | 1570-ZE-004 | Vendor | DCS | AI-HART-S | PLC | 4-20mA HART | PECS | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-TI-8806B | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | ------ | 1570-ZE-004 | Vendor | DCS | SOFTWARE | DCS | SOFT | PECS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-TSH-8806B | INTLK | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | ------ | 1570-ZE-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-TSL-8806B | DCS ALARM | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | ------ | 1570-ZE-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8806B | NEW | 1570-HS-8806B | VENDOR INTERFACE | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STANDBY) SA INLET | ------ | 1570-ZE-004 | Vendor | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8820 | NEW | 1570-TW-8820 | THERMOWELL | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | 4"-ACC-1570-8803-SBQ-FP-ET | 1570-ZE-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6016 | NEW | 1560-TE-6016 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5165 | LP STEAM TO SPRAY DESH | 16"-LPS-1560-6535-CBO-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8820 | NEW | 1570-TIT-8820 | TEMPERATURE INDICATING TRANSMITTER | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | ------ | 1570-ZE-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8820 | NEW | 1570-TI-8820 | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8821 | NEW | 1570-TW-8821 | THERMOWELL | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | 4"-ACC-1570-8804-SBQ-FP-ET | 1570-ZE-004 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6673 | NEW | 1560-TE-6673 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5166 | DESH OUTLET HP STEAM | 24"-HPS-1560-6104-AEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8821 | NEW | 1570-TIT-8821 | TEMPERATURE INDICATING TRANSMITTER | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | ------ | 1570-ZE-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-8821 | NEW | 1570-TI-8821 | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | ------ | 1570-ZE-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8815 | NEW | 1570-FE-8815 | FLOW ELEMENT - MAGNETIC | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | 4"-ACC-1570-8804-SBQ-FP-ET | 1570-ZE-004 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8815 | NEW | 1570-FIT-8815 | FLOW TRANSMITTER - MAGNETIC | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | ------ | 1570-ZE-004 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8815 | NEW | 1570-FI-8815 | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | ------ | 1570-ZE-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8815 | NEW | 1570-FSSL-8815 | INTLK | 1570-PR-PID-0000-EXP-5188 | ACID HEATER (STDBY) OUTLET | ------ | 1570-ZE-004 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8816 | NEW | 1570-FE-8816 | FLOW ELEMENT - MAGNETIC | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | 4"-ACC-1570-8803-SBQ-FP-ET | 1570-ZE-003 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8816 | NEW | 1570-FIT-8816 | FLOW TRANSMITTER - MAGNETIC | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | ------ | 1570-ZE-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8816 | NEW | 1570-FI-8816 | DCS INDICATION | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-8816 | NEW | 1570-FSSL-8816 | INTLK | 1570-PR-PID-0000-EXP-5188 | ACID HEATER OUTLET | ------ | 1570-ZE-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9008 | NEW | 1570-LIT-9008 | LEVEL TRANSMITTER - RADAR | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9008A | NEW | 1570-LI-9008A | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9008A | NEW | 1570-LAL-9008A | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9008A | NEW | 1570-LAH-9008A | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9008 | NEW | 1570-FI-9008 | FLOW GAUGE - ROTAMETER | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK |  | 1570-TK-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9009 | NEW | 1570-LIT-9009 | LEVEL TRANSMITTER - GWR | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-EQUIP | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9009 | NEW | 1570-LI-9009 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9009 | NEW | 1570-LAL-9009 | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9009 | NEW | 1570-LAH-9009 | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9009 | NEW | 1570-LSHH-9009 | INTLK | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9009 | NEW | 1570-LSLL-9009 | INTLK | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9009 | NEW | 1570-HS-9009 | DCS SELECTOR | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9009 | NEW | 1570-HAH-9009 | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9009 | NEW | 1570-HAL-9009 | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-HEV-9010 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-HV-9010 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | 6"-ACC-1570-7119-SBQ-- | 1570-TK-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-HS-9010A | DCS OPERATOR INITIATED CONTROL | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-ZAC-9010 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-ZAO-9010 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-ZSC-9010 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9010 | NEW | 1570-ZSO-9010 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-HS-9020 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | ------ | 1570-TK-003 | EXP | DCS | DCS | DCS | N/A | DCS | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-ZAC-9020 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-ZAO-9020 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-ZSC-9020 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-ZSO-9020 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-XEV-9020 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | ------ | 1570-TK-003 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9020 | NEW | 1570-XV-9020 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK TO CIRCULATION PUMPS | 8"-ACC-1520-7121-SBQ-FP-ET | 1570-TK-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-HEV-9011 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5192 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-HV-9011 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5192 | START-UP ACID STOR TK SA INLET | 4"-ACC-1570-7116-SBQ-FP-ET | 1570-TK-003 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | YES
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-HS-9011A | DCS OPERATOR INITIATED CONTROL | 1570-PR-PID-0000-EXP-5192 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-HS-9011B | PUSHBUTTON | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-ZAC-9011 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-ZAO-9011 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-ZSC-9011 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9011 | NEW | 1570-ZSO-9011 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5190 | START-UP ACID STOR TK SA INLET | ------ | 1570-TK-003 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-A-9041 | NEW | 1570-AE-9041 | SO2 AREA MONITOR | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | N/A | E-T | N/A | mV | FLD-OFFLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-A-9041 | NEW | 1570-AIT-9041 | SO2 AREA MONITOR | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-A-9041 | NEW | 1570-AI-9041 | DCS INDICATION | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-A-9041 | NEW | 1570-AAH-9041 | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-A-9041 | NEW | 1570-AAHH-9041 | DCS ALARM | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-A-9041 | NEW | 1570-ASH-9041 | INTLK | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7841 | NEW | 1540-XA-7841A | ALARM BEACON | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE ASSEMBLY | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1540 | CONTACT SECTION | 1540-X-7841 | NEW | 1540-XA-7841B | ALARM HORN | 1540-PR-PID-0000-EXP-5078 | 1540-ZP-007 JUG VALVE ASSEMBLY | ------ | N/A | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1540 | N | 1540-JBP-003 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9041A | NEW | 1570-XA-9041A | ALARM BEACON | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9041B | NEW | 1570-XA-9041B | ALARM HORN | 1570-PR-PID-0000-EXP-5190 | 1570-TK-003 START-UP ACID STORAGE TANK | ------ | 1570-TK-003 | EXP | DCS | DO | RIO | 24V | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-9200 | NEW | 1570-TW-9200 | THERMOWELL | 1570-PR-PID-0000-EXP-5192 | ACID TRUCKS LOADING ARMS HEADER | 10"-ACC-1570-7106-SBQ-- | N/A | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1560 | TURBO GENERATOR | 1560-T-6674 | NEW | 1560-TE-6674 | TEMPERATURE ELEMENT - TC TYPE K | 1560-PR-PID-0000-EXP-5166 | DESH BFW INLET | 4"-BFW-1560-6102-CEA-HC- | N/A | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1560 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-9200 | NEW | 1570-TIT-9200 | TEMPERATURE INDICATING TRANSMITTER | 1570-PR-PID-0000-EXP-5192 | ACID TRUCKS LOADING ARMS HEADER | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-T-9200 | NEW | 1570-TI-9200 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | ACID TRUCKS LOADING ARMS HEADER | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FE-9201 | FLOW ELEMENT - MAGNETIC | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | 6"-ACC-1570-7122-SBQ-- | 1570-ZM-001 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FIT-9201 | FLOW TRANSMITTER - MAGNETIC | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FIC-9201 | DCS INDICATION AND CONTROL | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FY-9201A | DCS CONTROL FUNCTION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FY-9201 | SMART VALVE POSITIONER | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FAL-9201 | DCS ALARM | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FAH-9201 | DCS ALARM | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FQI-9201 | DCS TOTALIZATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9201 | NEW | 1570-FCV-9201 | STRONG ACID CONTROL VALVE | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | 6"-ACC-1570-7122-SBQ-- | 1570-ZM-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-92202 | NEW | 1570-HS-9202A | DCS OPERATOR INITIATED CONTROL | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-92202 | NEW | 1570-HS-9202B | PUSHBUTTON | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9202 | NEW | 1570-HV-9202 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | 6"-ACC-1570-7122-SBQ-- | 1570-ZM-001 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9202 | NEW | 1570-HEV-9202 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9202 | NEW | 1570-ZSC-9202 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9202 | NEW | 1570-ZAC-9202 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9202 | NEW | 1570-ZSO-9202 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9202 | NEW | 1570-ZAO-9202 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9204 | NEW | 1570-ZS-9204 | LIMIT SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9204 | NEW | 1570-ZA-9204 | INTLK | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9203 | NEW | 1570-LSHH-9203 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9203 | NEW | 1570-LAHH-9203 | INTLK | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FE-9211 | FLOW ELEMENT - MAGNETIC | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | 6"-ACC-1570-7123-SBQ-- | 1570-ZM-002 | EXP | N/A | E-T | N/A | mV | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FIT-9211 | FLOW TRANSMITTER - MAGNETIC | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | 120 VAC/60 Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FIC-9211 | DCS INDICATION AND CONTROL | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FY-9211 | SMART VALVE POSITIONER | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | AO-HART | RIO | 4-20mA HART | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FCV-9211 | STRONG ACID CONTROL VALVE | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | 6"-ACC-1570-7123-SBQ-- | 1570-ZM-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FAH-9211 | DCS ALARM | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FAL-9211 | DCS ALARM | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FY-9211A | DCS CALCULATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-F-9211 | NEW | 1570-FQI-9211 | DCS TOTALIZATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-HV-9212 | ON/OFF VALVE | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | 6"-ACC-1570-7123-SBQ-- | 1570-ZM-002 | EXP | N/A | N/A | N/A | N/A | FLD-INLINE | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-HEV-9212 | PART OF VALVE SOLENOID VALVE | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DO | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-ZSC-9212 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-ZAC-9212 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-ZSO-9212 | PART OF VALVE LIMIT SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-ZAO-9212 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-HS-9212A | DCS OPERATOR INITIATED CONTROL | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | DCS | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9212 | NEW | 1570-HS-9212B | PUSHBUTTON | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | FLD-INT | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9214 | NEW | 1570-ZS-9214 | LIMIT SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-Z-9214 | NEW | 1570-ZA-9214 | INTLK | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9213 | NEW | 1570-LSHH-9213 | VENDOR SUPPLY LEVEL SWITCH - TUNING FORK | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9213 | NEW | 1570-LAHH-9213 | INTLK | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9215 | NEW | 1570-LIT-9215 | LEVEL TRANSMITTER - RADAR | 1570-PR-PID-0000-EXP-5192 | ACID LOADING AREA SUMP | ------ | N/A | EXP | DCS | AI-HART | RIO | 4-20mA HART | FLD-OFFLINE | 1570 | N | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9215 | NEW | 1570-LI-9215 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | ACID LOADING AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9215 | NEW | 1570-LAH-9215 | DCS ALARM | 1570-PR-PID-0000-EXP-5192 | ACID LOADING AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-L-9215 | NEW | 1570-LSHH-9215 | INTLK | 1570-PR-PID-0000-EXP-5192 | ACID LOADING AREA SUMP | ------ | N/A | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9220 | NEW | 1570-HS-9220B | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5192 | ACID TRUCK UNLOADING PUMP LOCAL STOP | ------ | 1570-PP-007 | EXP | N/A | DO | N/A | 24V | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9220 | NEW | 1570-JI-9220 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | ACID TRUCK UNLOADING PUMP POWER MONITOR | ------ | 1570-PP-007 | EXP | DCS | AI | DCS | 4-20mA | DCS | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-I-9220 | NEW | 1570-IAL-9220 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | ACID TRUCK UNLOADING PUMP LOW AMP SHUTDOWN | ------ | 1570-PP-007 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-H-9220 | NEW | 1570-HS-9220 | MOTOR CONTROL | 1570-PR-PID-0000-EXP-5192 | ACID TRUCK UNLOADING PUMP | ------ | 1570-PP-007 | EXP | DCS | SOFTWARE | PCR | SOFT | MCC | 1570 | N | SWRK | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9230 | NEW | 1570-XC-9230 | GROUND SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1570 | 120 VAC/60Hz | 1570-JBP-001 | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9230 | NEW | 1570-XI-9230 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 1 | ------ | 1570-ZM-001 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9231 | NEW | 1570-XC-9231 | GROUND SWITCH | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1570 | 120 VAC/60Hz | 1570-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9540 | NEW | 1510-XC-9540 | GROUND SWITCH | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING TRUCK GROUND SWITCH | ------ | 1510-TK-002 | EXP | DCS | DI | RIO | 24V | FLD-OFFLINE | 1510 | 120 VAC/60Hz | 1510-JBP-001 | NO
1500 | 1510 | LIQUID SULFUR | 1510-X-9540 | NEW | 1510-XI-9540 | DCS INDICATION | 1510-PR-PID-0000-EXP-5195 | CAUSTIC UNLOADING TRUCK GROUND SWITCH | ------ | 1510-TK-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1510 | N | N/A | NO
1500 | 1570 | SULFURIC ACID PRODUCT | 1570-X-9231 | NEW | 1570-XI-9231 | DCS INDICATION | 1570-PR-PID-0000-EXP-5192 | TRUCK LOADING BAY 2 | ------ | 1570-ZM-002 | EXP | DCS | SOFTWARE | DCS | SOFT | DCS | 1570 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1036 | NEW | 1540-TE-1036 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 2 RADIAL | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1036 | NEW | 1540-TI-1036 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 2 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1036 | NEW | 1540-TI-1036 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 2 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1040 | NEW | 1540-TE-1040 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1040 | NEW | 1540-TI-1040 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1040 | NEW | 1540-TI-1040 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1044 | NEW | 1540-TE-1044 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1044 | NEW | 1540-TI-1044 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1044 | NEW | 1540-TI-1044 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1038 | NEW | 1540-TE-1038 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 3 RADIAL | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1038 | NEW | 1540-TI-1038 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 3 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1038 | NEW | 1540-TI-1038 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 3 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1042 | NEW | 1540-TE-1042 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1042 | NEW | 1540-TI-1042 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1042 | NEW | 1540-TI-1042 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT BEARING 4 RADIAL | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1034 | NEW | 1540-TE-1034 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1034 | NEW | 1540-TI-1034 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1034 | NEW | 1540-TI-1034 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1006 | NEW | 1540-TE-1006 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1006 | NEW | 1540-TI-1006 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1006 | NEW | 1540-TI-1006 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1008 | NEW | 1540-TE-1008A | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL AXIAL | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1008 | NEW | 1540-TI-1008A | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL AXIAL | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1008 | NEW | 1540-TI-1008A | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL AXIAL | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1004 | NEW | 1540-TE-1004A | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1004 | NEW | 1540-TI-1004A | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | PLC | N/A | PLC | N/A | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1004 | NEW | 1540-TI-1004A | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL BEARING | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1097 | NEW | 1540-TE-1097 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | LUBE OIL TANK TEMPERATURE | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1097 | NEW | 1540-TIT-1097 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | LUBE OIL TANK TEMPERATURE | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1097 | NEW | 1540-TI-1097 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL TANK TEMPERATURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1113 | NEW | 1540-TE-1113 | TEMPERATURE ELEMENT - RTD PT-100 | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS AFTER COOLER TEMP | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | Ohm | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1113 | NEW | 1540-TIT-1113 | VENDOR SUPPLY TEMPERATURE INDICATING TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS AFTER COOLER TEMP | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-T-1113 | NEW | 1540-TI-1113 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS AFTER COOLER TEMP | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1101 | NEW | 1540-PDI-1101 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL FILTER DIFF PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1101 | NEW | 1540-PDIT-1101 | VENDOR SUPPLY PRESSURE TRANSMITTER - D/P | 1540-PR-PID-0000-EXP-5040 | LUBE OIL FILTER DIFF PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | NO | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1108 | NEW | 1540-PIT-1108 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1108 | NEW | 1540-PI-1108 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1108 | NEW | 1540-PAL-1108 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1108 | NEW | 1540-PSLL-1108 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1098 | NEW | 1540-PT-1098 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL MIST SEPERATOR | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1098 | NEW | 1540-PIT-1098 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | LUBE OIL MIST SEPERATOR | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1114 | NEW | 1540-PT-1114 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | SEAL GAS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1114 | NEW | 1540-PIT-1114 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | SEAL GAS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1064 | NEW | 1540-VYE-1064 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX PINON SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1072 | NEW | 1540-VYT-1072 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX PINON SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1048 | NEW | 1540-VXE-1048 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1056 | NEW | 1540-VXT-1056 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1068 | NEW | 1540-VYE-1068 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1076 | NEW | 1540-VYT-1076 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1052 | NEW | 1540-VXE-1052 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1060 | NEW | 1540-VXT-1060 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-S-1030 | NEW | 1540-SE-1030 | VENDOR SPPLY SPEED | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT SPEED | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-S-1032 | NEW | 1540-ST-1032 | VENDOR SUPPLY SPEED TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT SPEED | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-1078 | NEW | 1540-ZE-1078 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT AXIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-1080 | NEW | 1540-ZT-1080 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT AXIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1066 | NEW | 1540-VYE-1066 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1074 | NEW | 1540-VYT-1074 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1050 | NEW | 1540-VXE-1050 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1058 | NEW | 1540-VXT-1058 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1046 | NEW | 1540-VYE-1046 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX PINON SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1070 | NEW | 1540-VYT-1070 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX PINON SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1062 | NEW | 1540-VXE-1062 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | GEARBOX PINON SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1070 | NEW | 1540-VXT-1070 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | GEARBOX PINON SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-1026 | NEW | 1540-ZE-1026 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT AXIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-Z-1028 | NEW | 1540-ZT-1028 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT AXIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1020 | NEW | 1540-VYE-1020 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1024 | NEW | 1540-VYT-1024 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1012 | NEW | 1540-VXE-1012 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1016 | NEW | 1540-VXT-1016 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-S-1000 | NEW | 1540-SE-1000 | VENDOR SPPLY SPEED | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT SHAFT SPEED | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-S-1002 | NEW | 1540-ST-1002 | VENDOR SUPPLY SPEED TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT SHAFT SPEED | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1018 | NEW | 1540-VXE-1018 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1022 | NEW | 1540-VXT-1022 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1010 | NEW | 1540-VXE-1010 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1014 | NEW | 1540-VXT-1014 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1018 | NEW | 1540-VYE-1018 | VENDOR SUPPLY VIBRATION | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | N/A | N/A | N/A | N/A | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-V-1022 | NEW | 1540-VYT-1022 | VENDOR SUPPLY VIBRATION TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | COMP SHAFT RADIAL VIBRATION | ------ | 1540-GB-001 | Vendor | PLC | AI-S | PLC | 4-20mA | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1109 | NEW | 1540-PIT-1109 | VENDOR INTERFACE | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | SOFTWARE | PLC | SOFT | FLD-EQUIP | 1540 | N | N/A | NO
1500 | 1540 | CONTACT SECTION | 1540-P-1109 | NEW | 1540-PIT-1109 | VENDOR SUPPLY PRESSURE TRANSMITTER | 1540-PR-PID-0000-EXP-5040 | LUBE OIL SYS PRESSURE | ------ | 1540-GB-001 | Vendor | PLC | AI-HART | PLC | 4-20mA HART | FLD-EQUIP | 1540 | N | N/A | NO
Note on F824: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check in SPI Reply: Already added in SPI.
Note on F870: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be added to SA Valves package, handle as a Change
Note on F1075: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check in SPI as not all components seem to be in place properly yet we have assigned an I/O???? Reply: I/O from vendor added.
Note on F1100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need to assign the Closed Limit switch here? Reply: Added to SPI and index.
Note on F1394: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not part of 2810 package. Magnetostrictive LIT
Note on G1394: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Magnetostrictive LIT
Note on F1395: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not part of 2810 package. Magnetostrictive LIT
Note on G1395: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Magnetostrictive LIT
Note on F1774: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where is the TY-4822A and B??? It is in SPI that way.
Note on F1776: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where is the TY-4822A and B??? It is in SPI that way.
Note on F2062: Brent Cosgrove: line properties please!
Note on F2078: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on M2078: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid?
Note on N2078: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid?
Note on O2078: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid?
Note on P2078: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid?
Note on F2079: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on P2079: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid?
Note on P2080: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Position switch?
Note on P2081: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Position switch?
Note on F2086: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2088: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2095: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2135: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2140: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2141: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2150: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2167: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2174: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2181: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2209: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag in SPI index is 1560-TY-6018B. There will be one signal to control spray water(TBD after finalizing desuperheater package).
Note on G2211: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Spray Water Control Valve
Note on F2228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not found in SPI index
Note on F2235: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not found in SPI index
Note on F2240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not found in SPI index
Note on F2244: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index. Signals for valve solenoid and position switches to be added to index.
Note on F2245: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve position switch?
Note on F2246: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve position switch?
Note on F2247: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2248: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2249: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2250: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2251: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2252: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2253: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2254: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2255: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2256: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2264: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2267: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2272: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve solenoid signal?
Note on F2273: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve solenoid signal?
Note on F2274: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve Position switch? Needs IO
Note on F2275: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve Position switch? Needs IO
Note on F2276: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve Position switch? Needs IO
Note on F2277: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve Position switch? Needs IO
Note on F2278: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve Position switch? Needs IO
Note on F2279: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Valve Position switch? Needs IO
Note on F2280: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag to be created in SPI
Note on F2320: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Coud not find it in P&ID
Note on F2321: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Coud not find it in P&ID
Note on F2322: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Coud not find it in P&ID
Note on F2342: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jb? Could not be found in SP Index . Tag is 9317 in P&ID rev01.
Note on F2344: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jb? Could not be found in SP Index . Tag is 9318 in P&ID rev01.
Note on F2346: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Jb? Could not be found in SP Index . Tag is 9319 in P&ID rev01.
Note on F2375: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Could not be found in SPI index and P&ID.
Note on F2376: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Could not be found in SPI index and P&ID.
Note on F2481: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid and position switch signals to be added to index Reply: V4 config does not have switch.
Note on F2536: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index. Valve positioner signal to be added.
Note on F2749: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solenoid and position switch signals to be added. Reply: Added.
Note on H2750: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P&ID changed to 5192
Note on H2751: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P&ID changed to 5192
Note on H2752: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: P&ID changed to 5192
Note on F2789: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag not found in SPI index
Note on F2810: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TAG NOT FOUND IN SPI INDEX