## COVER PAGE
SE Global GmbH&Co.KG
SE TI STG EN EIC 2
SE TI STG EN EIC ITC
TURBINE CONTROL SYSTEM
SIGNAL EXCHANGE LIST
© Siemens Energy, 2021 All Rights Reserved Siemens Energy is a trademark licensed by Siemens AG
Goods labeled with "AL" not equal to "N" are subject to European or German export authorization when being exported out of the EU.Goods labeled with "ECCN" not equal to "N" are subject to US reexport authorization.
Even without a label, or with label "AL:N" or "ECCN:N", authorization may be required due to the final end-use and destination for which the goods are to be used.
|  |  |  | Date | 2025-11-11 | Project title: | Document title: | EXP Doc. No.: | RevA
|  |  |  | Created | Schmidt | Thacker Pass Project | TURBINE CONTROL SYSTEM SIGNAL EXCHANGE LIST
A | For approval | 2025-11-11 | Schmidt | Approved | J. Kolar |  |  | 1500-IN-VEN-4523-EXP-1301 | Language EN
Rev. | Remarks | Date | Name | ORIG. STANDARD REV F7 |  |  |  |  | Format A4

## SIGNAL EXCHANGE LIST
Project Rev_DCS_Coupling |  | Customer_TAG | Customer_Signalname | Project_KKS | Project_Signalname | English_Designation | English_Signal_Setting | Sub system | Type1_Signalsetting | Unit_Range_Low | Unit_Range_High | Unit_EU | XH54_Low_Alarm | XH52_Low_Warning | XH01_High_Warning | XH03_High_Alarm | Note | Table | Project_DCS_Type1 | Signal / Warning / Alarm / Fault [formula] | DCS Graphic [Yes / No] | Table | Criticality [High Medium Low] | Project_DCS_Type1 | Modbus Register | Modbus_BIT | write <- DCS read -> DCS | Type3 - Modbus | MODBUS-1_TCPIP-Address | MODBUS-2_TCPIP-Address
A | 1 | MAY10EV010 | XQ80 | MAY10EV010 | XQ80 | DCS COUPLING WATCHDOG | - |  | Signal | 0 | 100 |  |  |  |  | 1 |  |  | ANALOG SEND |  |  |  |  | ANALOG SEND | 40001 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XQ60 | MKA10CE069 | XQ60 | GENERATOR POWER OUTPUT | ACTIVE POWER | Power | Signal | -1.8 | 39.5 | MW |  |  |  |  | Alarm off digital |  | SINGLE ANALOG MEASUREMENT | Signal | Yes |  |  | SINGLE ANALOG MEASUREMENT | 40005 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XQ61 | MKA10CE069 | XQ61 | GENERATOR POWER OUTPUT | ACTIVE POWER |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40007 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XM20 | MKA10CE069 | XM20 | GENERATOR POWER OUTPUT | ACTIVE POWER | Power | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40007 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XH54 | MKA10CE069 | XH54 | GENERATOR POWER OUTPUT | ACTIVE POWER |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40007 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XH52 | MKA10CE069 | XH52 | GENERATOR POWER OUTPUT | ACTIVE POWER | Power | Warning low | 1 | bin | 0 |  | 3.437 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40007 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XH01 | MKA10CE069 | XH01 | GENERATOR POWER OUTPUT | ACTIVE POWER | Power | Warning high | 1 | bin | 0 |  |  | 3.437 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40007 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-JI-6521 | XH03 | MKA10CE069 | XH03 | GENERATOR POWER OUTPUT | ACTIVE POWER |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40007 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XQ60 | MAX10CL010 | XQ60 | CONTROL OIL TANK LEVEL | - | Oil | Signal | -5.94 | 5.67 | in |  |  |  |  | Alarm off digital |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40009 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XQ61 | MAX10CL010 | XQ61 | CONTROL OIL TANK LEVEL | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40011 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XM20 | MAX10CL010 | XM20 | CONTROL OIL TANK LEVEL | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40011 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XH54 | MAX10CL010 | XH54 | CONTROL OIL TANK LEVEL | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40011 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XH52 | MAX10CL010 | XH52 | CONTROL OIL TANK LEVEL | - | Oil | Warning low | 1 | bin | 0 |  | -1.93 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40011 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XH01 | MAX10CL010 | XH01 | CONTROL OIL TANK LEVEL | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40011 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LIT-6299 | XH03 | MAX10CL010 | XH03 | CONTROL OIL TANK LEVEL | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40011 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XQ60 | MAC10CP940 | XQ60 | LAST STAGE DIFFERENTIAL PRESSURE | - | Pressure | Signal | -3.63 | 36.26 | psi |  |  |  |  | Common Oil Sys Alarm | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40013 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XQ61 | MAC10CP940 | XQ61 | LAST STAGE DIFFERENTIAL PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40015 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XM20 | MAC10CP940 | XM20 | LAST STAGE DIFFERENTIAL PRESSURE | - | Pressure | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40015 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XH54 | MAC10CP940 | XH54 | LAST STAGE DIFFERENTIAL PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40015 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XH52 | MAC10CP940 | XH52 | LAST STAGE DIFFERENTIAL PRESSURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40015 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XH01 | MAC10CP940 | XH01 | LAST STAGE DIFFERENTIAL PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40015 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDI-6414 | XH03 | MAC10CP940 | XH03 | LAST STAGE DIFFERENTIAL PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40015 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XQ60 | MAX30CP010 | XQ60 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - | Oil | Signal | 0 | 116 | psi |  |  |  |  | Common Oil Sys Alarm | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40017 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XQ61 | MAX30CP010 | XQ61 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40019 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XM20 | MAX30CP010 | XM20 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40019 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XH54 | MAX30CP010 | XH54 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40019 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XH52 | MAX30CP010 | XH52 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40019 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XH01 | MAX30CP010 | XH01 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - | Oil | Warning high | 1 | bin | 0 |  |  | 87 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40019 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6310 | XH03 | MAX30CP010 | XH03 | CONTROL OIL FILTER DIFFERENTIAL PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40019 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XQ60 | MAX51CP020 | XQ60 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - | Oil | Signal | 0 | 116 | psi |  |  |  |  | Common Oil Sys Alarm | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40021 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XQ61 | MAX51CP020 | XQ61 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40023 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XM20 | MAX51CP020 | XM20 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40023 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XH54 | MAX51CP020 | XH54 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40023 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XH52 | MAX51CP020 | XH52 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40023 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XH01 | MAX51CP020 | XH01 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - | Oil | Warning high | 1 | bin | 0 |  |  | 50.76 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40023 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PDIT-6315 | XH03 | MAX51CP020 | XH03 | CONTROL OIL COOLER FILTER DIFFERENTIAL PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40023 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XQ60 | MAV35CP010 | XQ60 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - | Oil | Signal | 0 | 23.2 | psi |  |  |  |  | Common Oil Sys Alarm | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40025 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XQ61 | MAV35CP010 | XQ61 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40027 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XM20 | MAV35CP010 | XM20 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40027 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XH54 | MAV35CP010 | XH54 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40027 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XH52 | MAV35CP010 | XH52 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40027 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XH01 | MAV35CP010 | XH01 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - | Oil | Warning high | 1 | bin | 0 |  |  | 17.4 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40027 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PDIT-6324 | XH03 | MAV35CP010 | XH03 | LUBE OIL FILTER DIFFERENTIAL PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40027 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XQ60 | MAX40CP010 | XQ60 | TRIP OIL TEST PRESSURE | - | Oil | Signal | 0 | 3625 | psi(g) |  |  |  |  | Common Oil Sys Alarm | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40029 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XQ61 | MAX40CP010 | XQ61 | TRIP OIL TEST PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40031 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XM20 | MAX40CP010 | XM20 | TRIP OIL TEST PRESSURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40031 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XH54 | MAX40CP010 | XH54 | TRIP OIL TEST PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40031 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XH52 | MAX40CP010 | XH52 | TRIP OIL TEST PRESSURE | - | Oil | Warning low | 1 | bin | 0 |  | 1595 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40031 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XH01 | MAX40CP010 | XH01 | TRIP OIL TEST PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40031 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6311 | XH03 | MAX40CP010 | XH03 | TRIP OIL TEST PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40031 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XQ60 | LBD10CP010 | XQ60 | EXTRACTION PRESSURE | - | Pressure | Signal | -12.18 | 132.82 | psi(g) |  |  |  |  | Alarm off digital |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40033 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XQ61 | LBD10CP010 | XQ61 | EXTRACTION PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40035 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XM20 | LBD10CP010 | XM20 | EXTRACTION PRESSURE | - | Pressure | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40035 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XH54 | LBD10CP010 | XH54 | EXTRACTION PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40035 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XH52 | LBD10CP010 | XH52 | EXTRACTION PRESSURE | - | Pressure | Warning low | 1 | bin | 0 |  | 61.79 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40035 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XH01 | LBD10CP010 | XH01 | EXTRACTION PRESSURE | - | Pressure | Warning high | 1 | bin | 0 |  |  | 86.73 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40035 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6316 | XH03 | LBD10CP010 | XH03 | EXTRACTION PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40035 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XQ60 | LBB10CP010 | XQ60 | ADMISSION STEAM INLET PRESSURE | - | Pressure | Signal | 0 | 232 | psi(g) |  |  |  |  | Future N/A |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40037 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XQ61 | LBB10CP010 | XQ61 | ADMISSION STEAM INLET PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40039 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XM20 | LBB10CP010 | XM20 | ADMISSION STEAM INLET PRESSURE | - | Pressure | Fault | 1 | bin | 0 |  |  |  |  | Future N/A |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40039 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XH54 | LBB10CP010 | XH54 | ADMISSION STEAM INLET PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40039 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XH52 | LBB10CP010 | XH52 | ADMISSION STEAM INLET PRESSURE | - | Pressure | Warning low | 1 | bin | 0 |  | 89.2 |  |  | Future N/A |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40039 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XH01 | LBB10CP010 | XH01 | ADMISSION STEAM INLET PRESSURE | - | Pressure | Warning high | 1 | bin | 0 |  |  | 158.8 |  | Future N/A |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40039 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6320 | XH03 | LBB10CP010 | XH03 | ADMISSION STEAM INLET PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40039 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XQ60 | MAV70CP020 | XQ60 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - | Oil | Signal | 0 | 3625 | psi(g) |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40041 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XQ61 | MAV70CP020 | XQ61 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40043 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XM20 | MAV70CP020 | XM20 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40043 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XH54 | MAV70CP020 | XH54 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40043 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XH52 | MAV70CP020 | XH52 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - | Oil | Warning low | 1 | bin | 0 |  | 1160 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40043 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XH01 | MAV70CP020 | XH01 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40043 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6328 | XH03 | MAV70CP020 | XH03 | JACKING OIL CONTROL VALVE BLOCK INLET PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40043 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XQ60 | MAW40CP010 | XQ60 | REAR END SEAL STEAM PRESSURE | - | Seal | Signal | 0 | 3.63 | psi(g) |  |  |  |  | Alarm off digital |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40045 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XQ61 | MAW40CP010 | XQ61 | REAR END SEAL STEAM PRESSURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40047 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XM20 | MAW40CP010 | XM20 | REAR END SEAL STEAM PRESSURE | - | Seal | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40047 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XH54 | MAW40CP010 | XH54 | REAR END SEAL STEAM PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40047 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XH52 | MAW40CP010 | XH52 | REAR END SEAL STEAM PRESSURE | - | Seal | Warning low | 1 | bin | 0 |  | 0.22 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40047 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XH01 | MAW40CP010 | XH01 | REAR END SEAL STEAM PRESSURE | - | Seal | Warning high | 1 | bin | 0 |  |  | 1.45 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40047 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6329 | XH03 | MAW40CP010 | XH03 | REAR END SEAL STEAM PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40047 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XQ60 | MAC10CP040 | XQ60 | LAST STAGE INLET PRESSURE 1 | - | Pressure | Signal | 0 | 58 | psi(a) |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40049 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XQ61 | MAC10CP040 | XQ61 | LAST STAGE INLET PRESSURE 1 | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40051 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XM20 | MAC10CP040 | XM20 | LAST STAGE INLET PRESSURE 1 | - | Pressure | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40051 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XH54 | MAC10CP040 | XH54 | LAST STAGE INLET PRESSURE 1 | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40051 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XH52 | MAC10CP040 | XH52 | LAST STAGE INLET PRESSURE 1 | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40051 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XH01 | MAC10CP040 | XH01 | LAST STAGE INLET PRESSURE 1 | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40051 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6333 | XH03 | MAC10CP040 | XH03 | LAST STAGE INLET PRESSURE 1 | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40051 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XQ60 | MAC10CP041 | XQ60 | LAST STAGE INLET PRESSURE 2 | - | Pressure | Signal | 0 | 58 | psi(a) |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40053 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XQ61 | MAC10CP041 | XQ61 | LAST STAGE INLET PRESSURE 2 | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40055 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XM20 | MAC10CP041 | XM20 | LAST STAGE INLET PRESSURE 2 | - | Pressure | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40055 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XH54 | MAC10CP041 | XH54 | LAST STAGE INLET PRESSURE 2 | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40055 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XH52 | MAC10CP041 | XH52 | LAST STAGE INLET PRESSURE 2 | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40055 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XH01 | MAC10CP041 | XH01 | LAST STAGE INLET PRESSURE 2 | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40055 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6334 | XH03 | MAC10CP041 | XH03 | LAST STAGE INLET PRESSURE 2 | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40055 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XQ60 | MAD10CS910 | XQ60 | TURBINE SPEED | - | Speed | Signal | 0 | 8635 | rpm |  |  |  |  | Alarm off digital |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40057 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XQ61 | MAD10CS910 | XQ61 | TURBINE SPEED | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40059 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XM20 | MAD10CS910 | XM20 | TURBINE SPEED | - | Speed | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40059 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XH54 | MAD10CS910 | XH54 | TURBINE SPEED | - | Speed | Alarm low | 1 | bin | 0 | 4 | [5 empty] | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40059 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XH52 | MAD10CS910 | XH52 | TURBINE SPEED | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40059 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XH01 | MAD10CS910 | XH01 | TURBINE SPEED | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40059 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-SE-6390 | XH03 | MAD10CS910 | XH03 | TURBINE SPEED | - | Speed | Alarm high | 1 | bin | 0 |  |  |  | 7599 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40059 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XQ60 | MAA15CT910 | XQ60 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - | Monitoring | Signal | -200 | 200 | K |  |  |  |  | Pending Siemans ans | H | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40061 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XQ61 | MAA15CT910 | XQ61 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40063 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XM20 | MAA15CT910 | XM20 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40063 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XH54 | MAA15CT910 | XH54 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40063 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XH52 | MAA15CT910 | XH52 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - | Monitoring | Warning low | 1 | bin | 0 |  | -120 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40063 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XH01 | MAA15CT910 | XH01 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 120 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40063 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TDI-6412 | XH03 | MAA15CT910 | XH03 | TURBINE CASING TEMPERATURE - INSIDE/CENTER (CALCULATED) | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40063 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XQ60 | MAA15CT950 | XQ60 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - | Monitoring | Signal | -200 | 200 | K |  |  |  |  | Pending Siemans ans | H | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40065 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XQ61 | MAA15CT950 | XQ61 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40067 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XM20 | MAA15CT950 | XM20 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40067 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XH54 | MAA15CT950 | XH54 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40067 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XH52 | MAA15CT950 | XH52 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - | Monitoring | Warning low | 1 | bin | 0 |  | -40 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40067 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XH01 | MAA15CT950 | XH01 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 40 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40067 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TDI-6413 | XH03 | MAA15CT950 | XH03 | TURBINE CASING TEMPERATURE - TOP/BOTTOM (CALCULATED) | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40067 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XQ60 | MAX10CT010 | XQ60 | CONTROL OIL TANK TEMPERATURE | - | Oil | Signal | 32 | 212 | °F |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40069 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XQ61 | MAX10CT010 | XQ61 | CONTROL OIL TANK TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40071 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XM20 | MAX10CT010 | XM20 | CONTROL OIL TANK TEMPERATURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40071 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XH54 | MAX10CT010 | XH54 | CONTROL OIL TANK TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40071 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XH52 | MAX10CT010 | XH52 | CONTROL OIL TANK TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40071 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XH01 | MAX10CT010 | XH01 | CONTROL OIL TANK TEMPERATURE | - | Oil | Warning high | 1 | bin | 0 |  |  | 140 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40071 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6201 | XH03 | MAX10CT010 | XH03 | CONTROL OIL TANK TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40071 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XQ60 | MAD10CT010 | XQ60 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40073 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XQ61 | MAD10CT010 | XQ61 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40075 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XM20 | MAD10CT010 | XM20 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40075 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XH54 | MAD10CT010 | XH54 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40075 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XH52 | MAD10CT010 | XH52 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40075 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XH01 | MAD10CT010 | XH01 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40075 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6202 | XH03 | MAD10CT010 | XH03 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40075 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XQ60 | MAD10CT020 | XQ60 | LOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40077 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XQ61 | MAD10CT020 | XQ61 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40079 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XM20 | MAD10CT020 | XM20 | LOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40079 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XH54 | MAD10CT020 | XH54 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40079 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XH52 | MAD10CT020 | XH52 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40079 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XH01 | MAD10CT020 | XH01 | LOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40079 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6203 | XH03 | MAD10CT020 | XH03 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40079 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XQ60 | MAD10CT030 | XQ60 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40081 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XQ61 | MAD10CT030 | XQ61 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40083 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XM20 | MAD10CT030 | XM20 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40083 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XH54 | MAD10CT030 | XH54 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40083 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XH52 | MAD10CT030 | XH52 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40083 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XH01 | MAD10CT030 | XH01 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40083 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6204 | XH03 | MAD10CT030 | XH03 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40083 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XQ60 | MAD10CT011 | XQ60 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40085 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XQ61 | MAD10CT011 | XQ61 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40087 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XM20 | MAD10CT011 | XM20 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40087 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XH54 | MAD10CT011 | XH54 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40087 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XH52 | MAD10CT011 | XH52 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40087 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XH01 | MAD10CT011 | XH01 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40087 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6205 | XH03 | MAD10CT011 | XH03 | FRONT END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40087 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XQ60 | MAD10CT021 | XQ60 | LOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40089 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XQ61 | MAD10CT021 | XQ61 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40091 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XM20 | MAD10CT021 | XM20 | LOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40091 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XH54 | MAD10CT021 | XH54 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40091 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XH52 | MAD10CT021 | XH52 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40091 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XH01 | MAD10CT021 | XH01 | LOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40091 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6206 | XH03 | MAD10CT021 | XH03 | LOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40091 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XQ60 | MAD10CT031 | XQ60 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40093 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XQ61 | MAD10CT031 | XQ61 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40095 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XM20 | MAD10CT031 | XM20 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40095 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XH54 | MAD10CT031 | XH54 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40095 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XH52 | MAD10CT031 | XH52 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40095 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XH01 | MAD10CT031 | XH01 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40095 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6207 | XH03 | MAD10CT031 | XH03 | UNLOADED SIDE AXIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40095 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XQ60 | MAD20CT010 | XQ60 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40097 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XQ61 | MAD20CT010 | XQ61 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40099 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XM20 | MAD20CT010 | XM20 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40099 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XH54 | MAD20CT010 | XH54 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40099 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XH52 | MAD20CT010 | XH52 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40099 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XH01 | MAD20CT010 | XH01 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40099 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6208 | XH03 | MAD20CT010 | XH03 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40099 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XQ60 | MAD20CT011 | XQ60 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40101 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XQ61 | MAD20CT011 | XQ61 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40103 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XM20 | MAD20CT011 | XM20 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40103 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XH54 | MAD20CT011 | XH54 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40103 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XH52 | MAD20CT011 | XH52 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40103 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XH01 | MAD20CT011 | XH01 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 248 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40103 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6209 | XH03 | MAD20CT011 | XH03 | REAR END TURBINE RADIAL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40103 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XQ60 | MAD30CT010 | XQ60 | TURBINE END PINION BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40105 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XQ61 | MAD30CT010 | XQ61 | TURBINE END PINION BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40107 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XM20 | MAD30CT010 | XM20 | TURBINE END PINION BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40107 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XH54 | MAD30CT010 | XH54 | TURBINE END PINION BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40107 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XH52 | MAD30CT010 | XH52 | TURBINE END PINION BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40107 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XH01 | MAD30CT010 | XH01 | TURBINE END PINION BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 230 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40107 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6210 | XH03 | MAD30CT010 | XH03 | TURBINE END PINION BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40107 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XQ60 | MAD40CT010 | XQ60 | GENERATOR END PINION BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40109 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XQ61 | MAD40CT010 | XQ61 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40111 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XM20 | MAD40CT010 | XM20 | GENERATOR END PINION BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40111 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XH54 | MAD40CT010 | XH54 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40111 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XH52 | MAD40CT010 | XH52 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40111 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XH01 | MAD40CT010 | XH01 | GENERATOR END PINION BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 230 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40111 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6211 | XH03 | MAD40CT010 | XH03 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40111 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XQ60 | MAD50CT010 | XQ60 | TURBINE END WHEEL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40113 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XQ61 | MAD50CT010 | XQ61 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40115 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XM20 | MAD50CT010 | XM20 | TURBINE END WHEEL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40115 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XH54 | MAD50CT010 | XH54 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40115 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XH52 | MAD50CT010 | XH52 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40115 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XH01 | MAD50CT010 | XH01 | TURBINE END WHEEL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 221 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40115 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6212 | XH03 | MAD50CT010 | XH03 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40115 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XQ60 | MAD60CT010 | XQ60 | GENERATOR END WHEEL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40117 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XQ61 | MAD60CT010 | XQ61 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40119 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XM20 | MAD60CT010 | XM20 | GENERATOR END WHEEL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40119 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XH54 | MAD60CT010 | XH54 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40119 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XH52 | MAD60CT010 | XH52 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40119 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XH01 | MAD60CT010 | XH01 | GENERATOR END WHEEL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 221 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40119 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6213 | XH03 | MAD60CT010 | XH03 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40119 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XQ60 | MAD30CT011 | XQ60 | TURBINE END PINION BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40121 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XQ61 | MAD30CT011 | XQ61 | TURBINE END PINION BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40123 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XM20 | MAD30CT011 | XM20 | TURBINE END PINION BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40123 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XH54 | MAD30CT011 | XH54 | TURBINE END PINION BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40123 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XH52 | MAD30CT011 | XH52 | TURBINE END PINION BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40123 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XH01 | MAD30CT011 | XH01 | TURBINE END PINION BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 230 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40123 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6214 | XH03 | MAD30CT011 | XH03 | TURBINE END PINION BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40123 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XQ60 | MAD40CT011 | XQ60 | GENERATOR END PINION BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40125 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XQ61 | MAD40CT011 | XQ61 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40127 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XM20 | MAD40CT011 | XM20 | GENERATOR END PINION BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40127 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XH54 | MAD40CT011 | XH54 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40127 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XH52 | MAD40CT011 | XH52 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40127 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XH01 | MAD40CT011 | XH01 | GENERATOR END PINION BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 230 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40127 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6215 | XH03 | MAD40CT011 | XH03 | GENERATOR END PINION BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40127 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XQ60 | MAD50CT011 | XQ60 | TURBINE END WHEEL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40129 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XQ61 | MAD50CT011 | XQ61 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40131 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XM20 | MAD50CT011 | XM20 | TURBINE END WHEEL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40131 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XH54 | MAD50CT011 | XH54 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40131 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XH52 | MAD50CT011 | XH52 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40131 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XH01 | MAD50CT011 | XH01 | TURBINE END WHEEL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 221 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40131 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6216 | XH03 | MAD50CT011 | XH03 | TURBINE END WHEEL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40131 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XQ60 | MAD60CT011 | XQ60 | GENERATOR END WHEEL BEARING TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40133 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XQ61 | MAD60CT011 | XQ61 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40135 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XM20 | MAD60CT011 | XM20 | GENERATOR END WHEEL BEARING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40135 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XH54 | MAD60CT011 | XH54 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40135 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XH52 | MAD60CT011 | XH52 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40135 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XH01 | MAD60CT011 | XH01 | GENERATOR END WHEEL BEARING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 221 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40135 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6217 | XH03 | MAD60CT011 | XH03 | GENERATOR END WHEEL BEARING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40135 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XQ60 | MKD10CT010 | XQ60 | TURBINE END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40137 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XQ61 | MKD10CT010 | XQ61 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40139 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XM20 | MKD10CT010 | XM20 | TURBINE END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40139 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XH54 | MKD10CT010 | XH54 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40139 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XH52 | MKD10CT010 | XH52 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40139 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XH01 | MKD10CT010 | XH01 | TURBINE END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 194 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40139 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6218 | XH03 | MKD10CT010 | XH03 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40139 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XQ60 | MKD20CT010 | XQ60 | EXCITER END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40141 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XQ61 | MKD20CT010 | XQ61 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40143 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XM20 | MKD20CT010 | XM20 | EXCITER END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40143 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XH54 | MKD20CT010 | XH54 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40143 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XH52 | MKD20CT010 | XH52 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40143 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XH01 | MKD20CT010 | XH01 | EXCITER END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 194 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40143 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6219 | XH03 | MKD20CT010 | XH03 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40143 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XQ60 | MKD10CT011 | XQ60 | TURBINE END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40145 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XQ61 | MKD10CT011 | XQ61 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40147 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XM20 | MKD10CT011 | XM20 | TURBINE END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40147 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XH54 | MKD10CT011 | XH54 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40147 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XH52 | MKD10CT011 | XH52 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40147 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XH01 | MKD10CT011 | XH01 | TURBINE END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 194 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40147 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6220 | XH03 | MKD10CT011 | XH03 | TURBINE END GENERATOR RADIAL BEARING TEMP | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40147 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XQ60 | MKD20CT011 | XQ60 | EXCITER END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40149 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XQ61 | MKD20CT011 | XQ61 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40151 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XM20 | MKD20CT011 | XM20 | EXCITER END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40151 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XH54 | MKD20CT011 | XH54 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40151 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XH52 | MKD20CT011 | XH52 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40151 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XH01 | MKD20CT011 | XH01 | EXCITER END GENERATOR RADIAL BEARING TEMP | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 194 |  | Emerson 6500 |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40151 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6221 | XH03 | MKD20CT011 | XH03 | EXCITER END GENERATOR RADIAL BEARING TEMP | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40151 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XQ60 | MKA10CT010 | XQ60 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40153 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XQ61 | MKA10CT010 | XQ61 | STATOR WINDING PHASE U TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40155 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XM20 | MKA10CT010 | XM20 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40155 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XH54 | MKA10CT010 | XH54 | STATOR WINDING PHASE U TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40155 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XH52 | MKA10CT010 | XH52 | STATOR WINDING PHASE U TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40155 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XH01 | MKA10CT010 | XH01 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40155 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6222 | XH03 | MKA10CT010 | XH03 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40155 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XQ60 | MKA10CT011 | XQ60 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40157 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XQ61 | MKA10CT011 | XQ61 | STATOR WINDING PHASE U TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40159 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XM20 | MKA10CT011 | XM20 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40159 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XH54 | MKA10CT011 | XH54 | STATOR WINDING PHASE U TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40159 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XH52 | MKA10CT011 | XH52 | STATOR WINDING PHASE U TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40159 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XH01 | MKA10CT011 | XH01 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40159 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6223 | XH03 | MKA10CT011 | XH03 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40159 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XQ60 | MKA10CT020 | XQ60 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40161 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XQ61 | MKA10CT020 | XQ61 | STATOR WINDING PHASE V TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40163 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XM20 | MKA10CT020 | XM20 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40163 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XH54 | MKA10CT020 | XH54 | STATOR WINDING PHASE V TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40163 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XH52 | MKA10CT020 | XH52 | STATOR WINDING PHASE V TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40163 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XH01 | MKA10CT020 | XH01 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40163 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6224 | XH03 | MKA10CT020 | XH03 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40163 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XQ60 | MKA10CT021 | XQ60 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40165 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XQ61 | MKA10CT021 | XQ61 | STATOR WINDING PHASE V TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40167 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XM20 | MKA10CT021 | XM20 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40167 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XH54 | MKA10CT021 | XH54 | STATOR WINDING PHASE V TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40167 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XH52 | MKA10CT021 | XH52 | STATOR WINDING PHASE V TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40167 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XH01 | MKA10CT021 | XH01 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40167 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6225 | XH03 | MKA10CT021 | XH03 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40167 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XQ60 | MKA10CT030 | XQ60 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40169 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XQ61 | MKA10CT030 | XQ61 | STATOR WINDING PHASE W TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40171 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XM20 | MKA10CT030 | XM20 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40171 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XH54 | MKA10CT030 | XH54 | STATOR WINDING PHASE W TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40171 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XH52 | MKA10CT030 | XH52 | STATOR WINDING PHASE W TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40171 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XH01 | MKA10CT030 | XH01 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40171 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6226 | XH03 | MKA10CT030 | XH03 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40171 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XQ60 | MKA10CT031 | XQ60 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40173 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XQ61 | MKA10CT031 | XQ61 | STATOR WINDING PHASE W TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40175 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XM20 | MKA10CT031 | XM20 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40175 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XH54 | MKA10CT031 | XH54 | STATOR WINDING PHASE W TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40175 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XH52 | MKA10CT031 | XH52 | STATOR WINDING PHASE W TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40175 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XH01 | MKA10CT031 | XH01 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40175 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6227 | XH03 | MKA10CT031 | XH03 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40175 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XQ60 | MKA10CT012 | XQ60 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40177 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XQ61 | MKA10CT012 | XQ61 | STATOR WINDING PHASE U TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40179 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XM20 | MKA10CT012 | XM20 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40179 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XH54 | MKA10CT012 | XH54 | STATOR WINDING PHASE U TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40179 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XH52 | MKA10CT012 | XH52 | STATOR WINDING PHASE U TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40179 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XH01 | MKA10CT012 | XH01 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40179 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6228 | XH03 | MKA10CT012 | XH03 | STATOR WINDING PHASE U TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40179 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XQ60 | MKA10CT022 | XQ60 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40181 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XQ61 | MKA10CT022 | XQ61 | STATOR WINDING PHASE V TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40183 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XM20 | MKA10CT022 | XM20 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40183 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XH54 | MKA10CT022 | XH54 | STATOR WINDING PHASE V TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40183 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XH52 | MKA10CT022 | XH52 | STATOR WINDING PHASE V TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40183 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XH01 | MKA10CT022 | XH01 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40183 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6229 | XH03 | MKA10CT022 | XH03 | STATOR WINDING PHASE V TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40183 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XQ60 | MKA10CT032 | XQ60 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Signal | 32 | 392 | °F |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40185 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XQ61 | MKA10CT032 | XQ61 | STATOR WINDING PHASE W TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40187 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XM20 | MKA10CT032 | XM20 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40187 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XH54 | MKA10CT032 | XH54 | STATOR WINDING PHASE W TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40187 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XH52 | MKA10CT032 | XH52 | STATOR WINDING PHASE W TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40187 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XH01 | MKA10CT032 | XH01 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 257 |  | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40187 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6230 | XH03 | MKA10CT032 | XH03 | STATOR WINDING PHASE W TEMPERATURE | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 266 | Emerson 6500? Kurt |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40187 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XQ60 | MAV10CT020 | XQ60 | LUBE OIL TANK HEATING TEMPERATURE | - | Monitoring | Signal | 32 | 212 | °F |  |  |  |  | Analog in table only | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40189 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XQ61 | MAV10CT020 | XQ61 | LUBE OIL TANK HEATING TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40191 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XM20 | MAV10CT020 | XM20 | LUBE OIL TANK HEATING TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40191 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XH54 | MAV10CT020 | XH54 | LUBE OIL TANK HEATING TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40191 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XH52 | MAV10CT020 | XH52 | LUBE OIL TANK HEATING TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40191 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XH01 | MAV10CT020 | XH01 | LUBE OIL TANK HEATING TEMPERATURE | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 176 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40191 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6231 | XH03 | MAV10CT020 | XH03 | LUBE OIL TANK HEATING TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40191 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XQ60 | LBD10CT010 | XQ60 | EXTRACTION TEMPERATURE | - |  | Signal | 32 | 752 | °F |  |  |  |  | Analog value only |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40193 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XQ61 | LBD10CT010 | XQ61 | EXTRACTION TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40195 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XM20 | LBD10CT010 | XM20 | EXTRACTION TEMPERATURE | - |  | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40195 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XH54 | LBD10CT010 | XH54 | EXTRACTION TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40195 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XH52 | LBD10CT010 | XH52 | EXTRACTION TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40195 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XH01 | LBD10CT010 | XH01 | EXTRACTION TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40195 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6235 | XH03 | LBD10CT010 | XH03 | EXTRACTION TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40195 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XQ60 | MAL15CT010 | XQ60 | FLASH PIPE TEMPERATURE | - |  | Signal | 32 | 752 | °F |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40197 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XQ61 | MAL15CT010 | XQ61 | FLASH PIPE TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40199 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XM20 | MAL15CT010 | XM20 | FLASH PIPE TEMPERATURE | - |  | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40199 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XH54 | MAL15CT010 | XH54 | FLASH PIPE TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40199 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XH52 | MAL15CT010 | XH52 | FLASH PIPE TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40199 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XH01 | MAL15CT010 | XH01 | FLASH PIPE TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 239 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40199 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6236 | XH03 | MAL15CT010 | XH03 | FLASH PIPE TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40199 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XQ60 | MKA10CT060 | XQ60 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Signal | 32 | 392 | °F |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40201 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XQ61 | MKA10CT060 | XQ61 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40203 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XM20 | MKA10CT060 | XM20 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40203 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XH54 | MKA10CT060 | XH54 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40203 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XH52 | MKA10CT060 | XH52 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40203 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XH01 | MKA10CT060 | XH01 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 176 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40203 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6246 | XH03 | MKA10CT060 | XH03 | TURBINE END GENERATOR HOT AIR TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40203 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XQ60 | MAW40CT010 | XQ60 | REAR END SEAL STEAM TEMPERATURE | - |  | Signal | 32 | 752 | °F |  |  |  |  | Analog+Bit in Table | T | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40205 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XQ61 | MAW40CT010 | XQ61 | REAR END SEAL STEAM TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40207 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XM20 | MAW40CT010 | XM20 | REAR END SEAL STEAM TEMPERATURE | - |  | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40207 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XH54 | MAW40CT010 | XH54 | REAR END SEAL STEAM TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40207 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XH52 | MAW40CT010 | XH52 | REAR END SEAL STEAM TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | 437 |  |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40207 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XH01 | MAW40CT010 | XH01 | REAR END SEAL STEAM TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 509 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40207 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6247 | XH03 | MAW40CT010 | XH03 | REAR END SEAL STEAM TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40207 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XQ60 | MAA15CT010 | XQ60 | CASING FLANGE 50% TEMPERATURE | - | Monitoring | Signal | 32 | 1112 | °F |  |  |  |  | PLC only |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40209 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XQ61 | MAA15CT010 | XQ61 | CASING FLANGE 50% TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40211 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XM20 | MAA15CT010 | XM20 | CASING FLANGE 50% TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40211 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XH54 | MAA15CT010 | XH54 | CASING FLANGE 50% TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40211 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XH52 | MAA15CT010 | XH52 | CASING FLANGE 50% TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40211 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XH01 | MAA15CT010 | XH01 | CASING FLANGE 50% TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40211 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6250 | XH03 | MAA15CT010 | XH03 | CASING FLANGE 50% TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40211 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XQ60 | MAA15CT011 | XQ60 | CASING FLANGE 100% TEMPERATURE | - | Monitoring | Signal | 32 | 1112 | °F |  |  |  |  | PLC only |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40213 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XQ61 | MAA15CT011 | XQ61 | CASING FLANGE 100% TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40215 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XM20 | MAA15CT011 | XM20 | CASING FLANGE 100% TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40215 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XH54 | MAA15CT011 | XH54 | CASING FLANGE 100% TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40215 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XH52 | MAA15CT011 | XH52 | CASING FLANGE 100% TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40215 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XH01 | MAA15CT011 | XH01 | CASING FLANGE 100% TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40215 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6251 | XH03 | MAA15CT011 | XH03 | CASING FLANGE 100% TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40215 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XQ60 | MAA15CT050 | XQ60 | CASING WALL UPPER HALF TEMPERATURE | - | Monitoring | Signal | 32 | 1112 | °F |  |  |  |  | PLC only |  | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40217 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XQ61 | MAA15CT050 | XQ61 | CASING WALL UPPER HALF TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40219 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XM20 | MAA15CT050 | XM20 | CASING WALL UPPER HALF TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40219 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XH54 | MAA15CT050 | XH54 | CASING WALL UPPER HALF TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40219 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XH52 | MAA15CT050 | XH52 | CASING WALL UPPER HALF TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40219 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XH01 | MAA15CT050 | XH01 | CASING WALL UPPER HALF TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40219 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6253 | XH03 | MAA15CT050 | XH03 | CASING WALL UPPER HALF TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40219 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZI-6270 | XQ01 | MAA10CG050 | XQ01 | CONTROL VALVE 1 POSITION | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40221 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6271 | XQ01 | MAA10CG060 | XQ01 | CONTROL VALVE 2 POSITION | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40223 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZI-6272 | XQ01 | MAA10CG070 | XQ01 | CONTROL VALVE 3 POSITION | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40225 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6273 | XQ01 | MAA10CG080 | XQ01 | CONTROL VALVE 4 POSITION | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40227 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZI-6274 | XQ01 | MAC10CG010 | XQ01 | ROTARY SLIDE VALVE POSITION | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40229 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6275 | XQ01 | LBB10CG050 | XQ01 | ADMISSION STEAM CONTROL VALVE POSITION | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40231 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | XQ01 | MAA10AA460 | XQ01 | CONTROL VALVE 2 SERVO VALVE | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40233 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | XQ01 | MAA10AA470 | XQ01 | CONTROL VALVE 3 SERVO VALVE | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40235 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | XQ01 | MAA10AA480 | XQ01 | CONTROL VALVE 4 SERVO VALVE | VALVE POSITION | Control | Signal | 0 | 100 | % |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40237 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA93 | MAA10EC010 | XA93 | GROUP CONTROL TURBINE | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40239 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA94 | MAA10EC010 | XA94 | GROUP CONTROL TURBINE | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40241 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA93 | MAA10EC050 | XA93 | HP ACTUATING VALVE 1 MOVEMENT TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40243 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA94 | MAA10EC050 | XA94 | HP ACTUATING VALVE 1 MOVEMENT TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40245 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA93 | MAA10EC060 | XA93 | HP ACTUATING VALVE 2 MOVEMENT TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40247 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA94 | MAA10EC060 | XA94 | HP ACTUATING VALVE 2 MOVEMENT TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40249 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA94 | MAA10EC070 | XA94 | HP ACTUATING VALVE 3 MOVEMENT TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40251 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA93 | MAA10EC070 | XA93 | HP ACTUATING VALVE 3 MOVEMENT TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40253 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA93 | MAA10EC080 | XA93 | HP ACTUATING VALVE 4 MOVEMENT TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40255 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA94 | MAA10EC080 | XA94 | HP ACTUATING VALVE 4 MOVEMENT TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40257 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA93 | MAL10EC010 | XA93 | GROUP CONTROL DRAIN SYSTEM | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40259 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA94 | MAL10EC010 | XA94 | GROUP CONTROL DRAIN SYSTEM | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40261 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA93 | MAV10EC010 | XA93 | GROUP CONTROL OIL SYSTEM | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40263 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA94 | MAV10EC010 | XA94 | GROUP CONTROL OIL SYSTEM | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40265 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA93 | MAW10EC010 | XA93 | GROUP CONTROL GLAND STEAM | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40267 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA94 | MAW10EC010 | XA94 | GROUP CONTROL GLAND STEAM | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40269 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA94 | MAX10EC010 | XA94 | GROUP CONTROL HP OIL SYSTEM | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40271 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA93 | MAX10EC010 | XA93 | GROUP CONTROL HP OIL SYSTEM | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40273 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA94 | MAX40EC010 | XA94 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40275 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA93 | MAX40EC010 | XA93 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40277 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA94 | MAX40EC020 | XA94 | SGC TRIP ACTIVATION CHANNEL TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40279 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA93 | MAX40EC020 | XA93 | SGC TRIP ACTIVATION CHANNEL TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40281 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA94 | MAX40EC030 | XA94 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40283 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA93 | MAX40EC030 | XA93 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40285 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA93 | MAX40EC050 | XA93 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40287 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA94 | MAX40EC050 | XA94 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40289 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA94 | MAX40EC060 | XA94 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | ACTIVE STEP MONITORING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40291 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA93 | MAX40EC060 | XA93 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | ACTIVE STEP WAITING TIME (SGC) |  | Signal | - | - | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 40293 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | XT01 | MAY10DE020 | XT01 | LOAD CONTROLLER | REMAINING WARM UP TIME UNDER LOAD | Control | Signal | 0 | 600 | min |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40295 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020 | XQ01 | MAY10DS020 | XQ01 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | INTERFERENCE VALUE | Control | Signal | 0 | 1 | bin |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40297 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ44 | MAY10EU500 | YQ44 | KEY PERFORMANCE INDICATOR (KPI) | ACTIVE ENERGY (GWH) |  | Signal | 0 | 120000 | GWh |  |  |  |  | PLC only |  | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 40299 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XQ61 | MAY10CE215 | XQ61 | FIRE PROTECTION SIGNAL | active |  | Status | [9 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XG01 | MAY10CE215 | XG01 | FIRE PROTECTION SIGNAL | active |  | 2oo3 signal | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XB11 | MAY10CE215 | XB11 | FIRE PROTECTION SIGNAL | active |  | Single signal 1 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XB12 | MAY10CE215 | XB12 | FIRE PROTECTION SIGNAL | active |  | Single signal 2 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XB13 | MAY10CE215 | XB13 | FIRE PROTECTION SIGNAL | active |  | Single signal 3 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XM38 | MAY10CE215 | XM38 | FIRE PROTECTION SIGNAL | active |  | Fault | 1 | bin | 0 |  |  |  |  | Hard wired XS6211 - is soft bit redundant? Brent |  | 2oo3 BINARY MEASUREMENT | Fault |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XM01 | MAY10CE215 | XM01 | FIRE PROTECTION SIGNAL | active |  | Fault signal 1 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XM02 | MAY10CE215 | XM02 | FIRE PROTECTION SIGNAL | active |  | Fault signal 2 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CE215 | XM03 | MAY10CE215 | XM03 | FIRE PROTECTION SIGNAL | active |  | Fault signal 3 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40301 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XQ61 | MAY10EZ500 | XQ61 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Status | [9 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | ZT01 | MAY10EZ500 | ZT01 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | 2oo3 signal | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XB11 | MAY10EZ500 | XB11 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Single signal 1 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XB12 | MAY10EZ500 | XB12 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Single signal 2 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XB13 | MAY10EZ500 | XB13 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Single signal 3 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XM38 | MAY10EZ500 | XM38 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Fault | 1 | bin | 0 |  |  |  |  | Emerson 6500 |  | 2oo3 BINARY MEASUREMENT | Fault |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XM01 | MAY10EZ500 | XM01 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Fault signal 1 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XM02 | MAY10EZ500 | XM02 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Fault signal 2 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ500 | XM03 | MAY10EZ500 | XM03 | OVERSPEED PROTECTION | TRIP TO THE PROTECTION |  | Fault signal 3 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40302 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XQ61 | MKY10CE405 | XQ61 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Status | [9 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XG01 | MKY10CE405 | XG01 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | 2oo3 signal | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XB11 | MKY10CE405 | XB11 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Single signal 1 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XB12 | MKY10CE405 | XB12 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Single signal 2 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XB13 | MKY10CE405 | XB13 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Single signal 3 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XM38 | MKY10CE405 | XM38 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Fault | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT | Fault |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XM01 | MKY10CE405 | XM01 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Fault signal 1 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XM02 | MKY10CE405 | XM02 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Fault signal 2 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE405 | XM03 | MKY10CE405 | XM03 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 1 |  | Fault signal 3 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40303 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XQ61 | MKY10CE406 | XQ61 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Status | [9 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XG01 | MKY10CE406 | XG01 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | 2oo3 signal | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XB11 | MKY10CE406 | XB11 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Single signal 1 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XB12 | MKY10CE406 | XB12 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Single signal 2 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XB13 | MKY10CE406 | XB13 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Single signal 3 | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XM38 | MKY10CE406 | XM38 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Fault | 1 | bin | 0 | [6 empty] | 2oo3 BINARY MEASUREMENT | Fault |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XM01 | MKY10CE406 | XM01 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Fault signal 1 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XM02 | MKY10CE406 | XM02 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Fault signal 2 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE406 | XM03 | MKY10CE406 | XM03 | GENERATOR PROTECTION | TRIPPING COMMAND TURBINE STOP VALVE TRIP COIL 2 |  | Fault signal 3 | 1 | bin | 0 |  |  |  |  | 2oo3 voting | T | 2oo3 BINARY MEASUREMENT |  |  |  |  | 2oo3 BINARY MEASUREMENT | 40304 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | XA61 | CBP10CE101 | XA61 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40313 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | XA01 | CBP10CE101 | XA01 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40313 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | XA02 | CBP10CE101 | XA02 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40313 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | XA03 | CBP10CE101 | XA03 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40313 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | XA04 | CBP10CE101 | XA04 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40313 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | XA61 | CBP10CE108 | XA61 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40314 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | XA01 | CBP10CE108 | XA01 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40314 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | XA02 | CBP10CE108 | XA02 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40314 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | XA03 | CBP10CE108 | XA03 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40314 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | XA04 | CBP10CE108 | XA04 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40314 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | XA61 | CBP10CE110 | XA61 | SYNCHRONIZATION | REMOTE RESET LOR |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40315 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | XA01 | CBP10CE110 | XA01 | SYNCHRONIZATION | REMOTE RESET LOR |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40315 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | XA02 | CBP10CE110 | XA02 | SYNCHRONIZATION | REMOTE RESET LOR |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40315 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | XA03 | CBP10CE110 | XA03 | SYNCHRONIZATION | REMOTE RESET LOR |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40315 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | XA04 | CBP10CE110 | XA04 | SYNCHRONIZATION | REMOTE RESET LOR |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40315 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | XA61 | CBP10CE111 | XA61 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40316 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | XA01 | CBP10CE111 | XA01 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40316 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | XA02 | CBP10CE111 | XA02 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40316 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | XA03 | CBP10CE111 | XA03 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40316 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | XA04 | CBP10CE111 | XA04 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40316 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | XA61 | LBB10EE010 | XA61 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40317 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | XA01 | LBB10EE010 | XA01 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40317 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | XA02 | LBB10EE010 | XA02 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40317 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | XA03 | LBB10EE010 | XA03 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40317 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | XA04 | LBB10EE010 | XA04 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40317 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | XA61 | LBB10EE011 | XA61 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40318 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | XA01 | LBB10EE011 | XA01 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40318 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | XA02 | LBB10EE011 | XA02 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40318 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | XA03 | LBB10EE011 | XA03 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40318 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | XA04 | LBB10EE011 | XA04 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40318 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | XA61 | LBE10EE010 | XA61 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40319 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | XA01 | LBE10EE010 | XA01 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40319 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | XA02 | LBE10EE010 | XA02 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40319 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | XA03 | LBE10EE010 | XA03 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40319 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | XA04 | LBE10EE010 | XA04 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40319 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | XA61 | MAA10EE010 | XA61 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40320 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | XA01 | MAA10EE010 | XA01 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40320 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | XA02 | MAA10EE010 | XA02 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40320 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | XA03 | MAA10EE010 | XA03 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40320 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | XA04 | MAA10EE010 | XA04 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40320 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | XA61 | MAV10EE011 | XA61 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40321 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | XA01 | MAV10EE011 | XA01 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40321 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | XA02 | MAV10EE011 | XA02 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40321 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | XA03 | MAV10EE011 | XA03 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40321 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | XA04 | MAV10EE011 | XA04 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40321 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | XA61 | MAW10EE010 | XA61 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40322 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | XA01 | MAW10EE010 | XA01 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40322 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | XA02 | MAW10EE010 | XA02 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40322 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | XA03 | MAW10EE010 | XA03 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40322 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | XA04 | MAW10EE010 | XA04 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40322 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | XA61 | MAX40EE010 | XA61 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40323 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | XA01 | MAX40EE010 | XA01 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40323 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | XA02 | MAX40EE010 | XA02 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40323 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | XA03 | MAX40EE010 | XA03 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40323 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | XA04 | MAX40EE010 | XA04 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40323 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | XA61 | MAY10DS020 | XA61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40324 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | XA01 | MAY10DS020 | XA01 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40324 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | XA02 | MAY10DS020 | XA02 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40324 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | XA03 | MAY10DS020 | XA03 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40324 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | XA04 | MAY10DS020 | XA04 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40324 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | XA61 | MAY10DS021 | XA61 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40325 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | XA01 | MAY10DS021 | XA01 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40325 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | XA02 | MAY10DS021 | XA02 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40325 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | XA03 | MAY10DS021 | XA03 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40325 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | XA04 | MAY10DS021 | XA04 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40325 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | XA61 | MAY10EE010 | XA61 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40326 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | XA01 | MAY10EE010 | XA01 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40326 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | XA02 | MAY10EE010 | XA02 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40326 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | XA03 | MAY10EE010 | XA03 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40326 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | XA04 | MAY10EE010 | XA04 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40326 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | XA61 | MAY10EE020 | XA61 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40327 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | XA01 | MAY10EE020 | XA01 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40327 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | XA02 | MAY10EE020 | XA02 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40327 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | XA03 | MAY10EE020 | XA03 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40327 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | XA04 | MAY10EE020 | XA04 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40327 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | XA61 | MAY10EE030 | XA61 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40328 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | XA01 | MAY10EE030 | XA01 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40328 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | XA02 | MAY10EE030 | XA02 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40328 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | XA03 | MAY10EE030 | XA03 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40328 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | XA04 | MAY10EE030 | XA04 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40328 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | XA61 | MAY10EE220A | XA61 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40329 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | XA01 | MAY10EE220A | XA01 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40329 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | XA02 | MAY10EE220A | XA02 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40329 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | XA03 | MAY10EE220A | XA03 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40329 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | XA04 | MAY10EE220A | XA04 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40329 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | XA61 | MAY10EE910 | XA61 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40330 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | XA01 | MAY10EE910 | XA01 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40330 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | XA02 | MAY10EE910 | XA02 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40330 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | XA03 | MAY10EE910 | XA03 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40330 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | XA04 | MAY10EE910 | XA04 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40330 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | XA61 | MAY10EE920 | XA61 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40331 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | XA01 | MAY10EE920 | XA01 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40331 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | XA02 | MAY10EE920 | XA02 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40331 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | XA03 | MAY10EE920 | XA03 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40331 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | XA04 | MAY10EE920 | XA04 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40331 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | XA61 | MKY10EE230 | XA61 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40332 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | XA01 | MKY10EE230 | XA01 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40332 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | XA02 | MKY10EE230 | XA02 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40332 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | XA03 | MKY10EE230 | XA03 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40332 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | XA04 | MKY10EE230 | XA04 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40332 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | XA61 | MKY10EE231 | XA61 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40333 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | XA01 | MKY10EE231 | XA01 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40333 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | XA02 | MKY10EE231 | XA02 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40333 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | XA03 | MKY10EE231 | XA03 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40333 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | XA04 | MKY10EE231 | XA04 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40333 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | XA61 | MKY10EE232 | XA61 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40334 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | XA01 | MKY10EE232 | XA01 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40334 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | XA02 | MKY10EE232 | XA02 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40334 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | XA03 | MKY10EE232 | XA03 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40334 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | XA04 | MKY10EE232 | XA04 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40334 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | XA61 | MKY10EE233 | XA61 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40335 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | XA01 | MKY10EE233 | XA01 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40335 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | XA02 | MKY10EE233 | XA02 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40335 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | XA03 | MKY10EE233 | XA03 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40335 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | XA04 | MKY10EE233 | XA04 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40335 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | XA61 | MKY10EE234 | XA61 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40336 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | XA01 | MKY10EE234 | XA01 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40336 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | XA02 | MKY10EE234 | XA02 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40336 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | XA03 | MKY10EE234 | XA03 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40336 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | XA04 | MKY10EE234 | XA04 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40336 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | XA61 | MKY10EE235 | XA61 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40337 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | XA01 | MKY10EE235 | XA01 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40337 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | XA02 | MKY10EE235 | XA02 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40337 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | XA03 | MKY10EE235 | XA03 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40337 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | XA04 | MKY10EE235 | XA04 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40337 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | XA61 | MKY10EE236 | XA61 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40338 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | XA01 | MKY10EE236 | XA01 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40338 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | XA02 | MKY10EE236 | XA02 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40338 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | XA03 | MKY10EE236 | XA03 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40338 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | XA04 | MKY10EE236 | XA04 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40338 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | XA61 | MKY10EE237 | XA61 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40339 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | XA01 | MKY10EE237 | XA01 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40339 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | XA02 | MKY10EE237 | XA02 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40339 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | XA03 | MKY10EE237 | XA03 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40339 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | XA04 | MKY10EE237 | XA04 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40339 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | XA61 | MKY10EE245 | XA61 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40340 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | XA01 | MKY10EE245 | XA01 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40340 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | XA02 | MKY10EE245 | XA02 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40340 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | XA03 | MKY10EE245 | XA03 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40340 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | XA04 | MKY10EE245 | XA04 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40340 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | XA61 | MKY10EE247 | XA61 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Status | [7 empty] | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40341 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | XA01 | MKY10EE247 | XA01 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Feedback on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40341 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | XA02 | MKY10EE247 | XA02 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Feedback off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40341 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | XA03 | MKY10EE247 | XA03 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Release on | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40341 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | XA04 | MKY10EE247 | XA04 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Release off | 1 | bin | 0 |  |  |  |  | PLC only |  | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 40341 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LSH-6340 | XG51 | MKA10CL220 | XG51 | EXCITER END GENERATOR PAN LEAKAGE WATER LEVEL | NO WARNING |  | Signal | 1 | bin | 0 |  |  |  |  | Alarm | T | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LSH-6343 | XG51 | MKA10CL210 | XG51 | TURBINE END GENERATOR PAN LEAKAGE WATER LEVEL | NO WARNING |  | Signal | 1 | bin | 0 |  |  |  |  | Alarm | T | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LSH-6345 | XG01 | MAM10CL210 | XG01 | GLAND STEAM CONDENSER CONDENSATE LEVEL IN SIPHON | - |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6312 | ZT01 | MAX40CP920 | ZT01 | TRIP OIL PRESSURE | TURBINE IS TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6317 | XB13 | MAC10CP950 | XB13 | EXHAUST STEAM PRESSURE | ALARM |  | Signal | 1 | bin | 0 |  |  |  |  | Ask where the rest of the 2oo3 Alarms are |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6317 | XB11 | MAC10CP950 | XB11 | EXHAUST STEAM PRESSURE | ALARM |  | Signal | 1 | bin | 0 |  |  |  |  | Ask where the rest of the 2oo3 Alarms are |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6317 | ZT01 | MAC10CP950 | ZT01 | EXHAUST STEAM PRESSURE | TRIP BY EXHAUST STEAM PRESSURE, ALARM |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6317 | XB12 | MAC10CP950 | XB12 | EXHAUST STEAM PRESSURE | ALARM |  | Signal | 1 | bin | 0 |  |  |  |  | Ask where the rest of the 2oo3 Alarms are |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-SE-6390 | ZV01 | MAD10CS910 | ZV01 | TURBINE SPEED | ACTIVE TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-SE-6390 | XH03 | MAD10CS910 | XH03 | TURBINE SPEED | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  | - |  |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XB13 | MAC10CT950 | XB13 | EXHAUST STEAM TEMPERATURE | ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XB11 | MAC10CT950 | XB11 | EXHAUST STEAM TEMPERATURE | ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XB12 | MAC10CT950 | XB12 | EXHAUST STEAM TEMPERATURE | ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZIC-6260 | XG01 | MAA10CG210 | XG01 | EMERGENCY STOP VALVE 1 CLOSED POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZIC-6282 | XG01 | MAA10CG213 | XG01 | EMERGENCY STOP VALVE 1 CLOSED POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZIC-6284 | XG01 | LBB10CG211 | XG01 | ADMISSION STEAM ESV CLOSED POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40343 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZIC-6285 | XG01 | LBB10CG212 | XG01 | ADMISSION STEAM ESV CLOSED POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZIC-6286 | XG02 | MAK40CG210 | XG02 | COVER HOOD CLOSED POSITION | CLOSED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZIC-6406 | XG02 | LBB10CG240 | XG02 | EMERGENCY STOP FLAP DRAIN VALVE CLOSED POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZIO-6281 | XG01 | MAA10CG211 | XG01 | EMERGENCY STOP VALVE 1 OPEN POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZIO-6283 | XG01 | LBB10CG210 | XG01 | ADMISSION STEAM ESV OPEN POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZIO-6407 | XG01 | LBB10CG241 | XG01 | EMERGENCY STOP FLAP DRAIN VALVE OPEN POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | BJA10CE306 | XB11 | BJA10CE306 | XB11 | MCC CABINET SIGNALISATION | ALL MCBS FOR ET200SP HA ARE CLOSED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | BJA10CE307 | XB11 | BJA10CE307 | XB11 | MCC CABINET SIGNALISATION | 24VDC FOR ET200SP HA IS OK |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE001 | XG01 | CBP10CE001 | XG01 | GCP PROTECTION DEVICE (F1) ALARM SUMMARY | ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE002 | XG01 | CBP10CE002 | XG01 | GCP PROTECTION DEVICE (F1) TRIP SUMMARY | ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE003 | XG01 | CBP10CE003 | XG01 | GCP PROTECTION DEVICE (-F2) ALARM SUMMARY | ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE004 | XG01 | CBP10CE004 | XG01 | GCP PROTECTION DEVICE (-F2) TRIP SUMMARY | ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE005 | XG01 | CBP10CE005 | XG01 | INTERNAL FAILURE OF PROTECTION (-F1) | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE006 | XG01 | CBP10CE006 | XG01 | INTERNAL FAILURE OF PROTECTION (-F2) | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE008 | XG11 | CBP10CE008 | XG11 | SYNCHRONIZATION | SYNCHRONIZER INTERNAL FAILURE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE009 | XB11 | CBP10CE009 | XB11 | ANY MCB IN PROTECTION PANEL(CBP10.1) IS OFF | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40344 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE010 | XB11 | CBP10CE010 | XB11 | LOSS OF SUPPLY VOLTAGE FOR PROTECTION (-F1,F2) | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE012 | XB11 | CBP10CE012 | XB11 | ANY MCB IN SYNCHRONIZATION CUBICLE (CBP10) IS OFF | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE013 | XG01 | CBP10CE013 | XG01 | LOSS OF SUPPLY VOLTAGE FOR SYNCHRONIZATION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE014 | XB11 | CBP10CE014 | XB11 | LOSS OF SYNCHRONIZED VOLTAGE | ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE016 | XG01 | CBP10CE016 | XG01 | SYNCHRONIZATION | REMOTE SYNCHRONIZATIN SELECTED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE018 | XB02 | CBP10CE018 | XB02 | GENERATOR CIRCUIT BREAKER | FEEDBACK OPEN |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE019 | XB02 | CBP10CE019 | XB02 | GENERATOR CIRCUIT BREAKER EARTHING SWITCH | FEEDBACK OPEN |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE021 | XB02 | CBP10CE021 | XB02 | MEDIUM VOLTAGE DISTRIBUTION CIRCUIT BREAKER 2 | FEEDBACK OPEN |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE025 | XB11 | CBP10CE025 | XB11 | ANY MCB FOR SYNCHRONIZING VOLTAGE IS OFF | ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE032 | XB11 | CBP10CE032 | XB11 | LOR NOT ACTIVATED | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE033 | XB11 | CBP10CE033 | XB11 | START BOX DC POWER INLETS ARE OFF | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE034 | XB11 | CBP10CE034 | XB11 | START BOX MCB'S OF DC POWER OUTLETS ARE OK | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE112 | YB01 | CBP10CE112 | YB01 | SYNCHRONIZATION | PARALLEL WITH GRID |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE306 | XG01 | CBP10CE306 | XG01 | GENERATOR CONTROL PANEL SIGNALISATION | FAULT OF ET200SP HA POWER SUPPLY MCB |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CJJ10CT010 | XQ01 | CJJ10CT010 | XQ01 | TCS SIGNALISATION INDOOR TEMPERATURE | - |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CJJ10GS010 | XM55 | CJJ10GS010 | XM55 | TCS SIGNALISATION | DOORS OPEN |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40345 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CJJ10GS010 | XM54 | CJJ10GS010 | XM54 | TCS SIGNALISATION | NO CB FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CJJ10GS010 | YT61 | CJJ10GS010 | YT61 | TCS SIGNALISATION | RMS ACCESS ALLOWED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CJJ10GS010 | XM56 | CJJ10GS010 | XM56 | TCS SIGNALISATION | PS FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CJJ10GS010 | XM14 | CJJ10GS010 | XM14 | TCS SIGNALISATION | SCALANCE FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA450 | XC98 | LBB10AA450 | XC98 | ADMISSION STEAM CONTROL VALVE | READY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA450 | XC42 | LBB10AA450 | XC42 | ADMISSION STEAM CONTROL VALVE | IN POSITION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD10CP920 | XB11 | LBD10CP920 | XB11 | EXTRACTION STEAM PRESSURE SWITCH VOTER 2 CHANNEL 1 | ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD10CP920 | XG01 | LBD10CP920 | XG01 | EXTRACTION E1 PRESSURE | TRIP VOTER 2 |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD10CP920 | XB13 | LBD10CP920 | XB13 | EXTRACTION STEAM PRESSURE SWITCH VOTER 2 CHANNEL 3 | ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD10CP920 | XB12 | LBD10CP920 | XB12 | EXTRACTION STEAM PRESSURE SWITCH VOTER 2 CHANNEL 2 | ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | XC42 | MAA10AA450 | XC42 | CONTROL VALVE 1 SERVO VALVE | IN POSITION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | XC98 | MAA10AA450 | XC98 | CONTROL VALVE 1 SERVO VALVE | READY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | XC42 | MAA10AA460 | XC42 | CONTROL VALVE 2 SERVO VALVE | IN POSITION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | XC98 | MAA10AA460 | XC98 | CONTROL VALVE 2 SERVO VALVE | READY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | XC42 | MAA10AA470 | XC42 | CONTROL VALVE 3 SERVO VALVE | IN POSITION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | XC98 | MAA10AA470 | XC98 | CONTROL VALVE 3 SERVO VALVE | READY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40346 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | XC42 | MAA10AA480 | XC42 | CONTROL VALVE 4 SERVO VALVE | IN POSITION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | XC98 | MAA10AA480 | XC98 | CONTROL VALVE 4 SERVO VALVE | READY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | YV03 | MAA10EC010 | YV03 | GROUP CONTROL TURBINE TO DCS | START INLET STEAM PREHEATING |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XV01 | MAA10EC050 | XV01 | HP ACTUATING VALVE 1 MOVEMENT TEST | TEST HAS TO BE EXECUTED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XV01 | MAA10EC060 | XV01 | HP ACTUATING VALVE 2 MOVEMENT TEST | TEST HAS TO BE EXECUTED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XV01 | MAA10EC070 | XV01 | HP ACTUATING VALVE 3 MOVEMENT TEST | TEST HAS TO BE EXECUTED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XV01 | MAA10EC080 | XV01 | HP ACTUATING VALVE 4 MOVEMENT TEST | TEST HAS TO BE EXECUTED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAC10AA410 | XC98 | MAC10AA410 | XC98 | EXTRACTION E1 CONTROL VALVE 1 SERVO VALVE | READY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAC10AA410 | XC42 | MAC10AA410 | XC42 | EXTRACTION E1 CONTROL VALVE 1 SERVO VALVE | IN POSITION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAD10EZ010 | ZT01 | MAD10EZ010 | ZT01 | SPEED TRANSIENT PROTECTION | ACTIVE TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | XB50 | MAV25AP110 | XB50 | EMERGENCY OIL PUMP | NO OVERLOAD |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | XV01 | MAX20EE010 | XV01 | DCO CONTROL OIL PUMPS | NO AUTOMATIC MODE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | XV02 | MAX20EE010 | XV02 | DCO CONTROL OIL PUMPS | BOTH DEVICES RUNNING |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10CH220 | XL63 | MAY10CH220 | XL63 | MANUAL TRIP PUSH BUTTON 1, ALARM | INITIATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10CH230 | XL63 | MAY10CH230 | XL63 | MANUAL TRIP PUSH BUTTON 2, ALARM | INITIATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XT02 | MAY10DE020 | XT02 | LOAD CONTROLLER | WARM UP UNDER LOAD COMPLETED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40347 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DU940 | XT01 | MAY10DU940 | XT01 | HP MIN VALVE POSITION | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | XC15 | MAY10EE020 | XC15 | LOAD CONTROLLER SELECTION | BLOCKED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | XC15 | MAY10EE030 | XC15 | INLET PRESSURE CONTROLLER SELECTION | BLOCKED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE110 | XA01 | MAY10EE110 | XA01 | DCS MASTER RELEASE | ON |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | XA14 | MAY10EE910 | XA14 | TURBINE STARTUP, START | ENABLE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EK300 | XG01 | MAY10EK300 | XG01 | EXTERNAL TRIP | TRIP VOTER 6 |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EK500 | XG01 | MAY10EK500 | XG01 | OVERSPEED PROTECTION | OVERSPEED TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EK540 | XM14 | MAY10EK540 | XM14 | OVERSPEED PROTECTION | FAILURE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU020 | XG01 | MAY10EU020 | XG01 | ISLAND MODE TURBINE-SET | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EY010 | ZT01 | MAY10EY010 | ZT01 | CASING TEMPERATURE PROTECTION | TURBINE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK64 | MAY10EZ010 | ZK64 | 1560-TIT-6255 ADMISSION STEAM INLET TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK63 | MAY10EZ010 | ZK63 | 1560-TE-6230 STATOR WINDING PHASE W TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK62 | MAY10EZ010 | ZK62 | 1560-TE-6227 STATOR WINDING PHASE W TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK61 | MAY10EZ010 | ZK61 | 1560-TE-6226 STATOR WINDING PHASE W TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK60 | MAY10EZ010 | ZK60 | 1560-TE-6229 STATOR WINDING PHASE V TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK56 | MAY10EZ010 | ZK56 | 1560-TE-6223 STATOR WINDING PHASE U TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40348 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK59 | MAY10EZ010 | ZK59 | 1560-TE-6225 STATOR WINDING PHASE V TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK45 | MAY10EZ010 | ZK45 | 1560-VT-6383 EXCITER END GENERATOR VERTICAL BEARING VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK68 | MAY10EZ010 | ZK68 | 1560-LI-6278 DRAIN TANK LEVEL | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK19 | MAY10EZ010 | ZK19 | MAY10CH210 TURBINE EMERGENCY STOP (TURBINE HALL) | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK58 | MAY10EZ010 | ZK58 | 1560-TE-6224 STATOR WINDING PHASE V TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK57 | MAY10EZ010 | ZK57 | 1560-TE-6228 STATOR WINDING PHASE U TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK67 | MAY10EZ010 | ZK67 | 1560-TI-6256 EMERGENCY STOP VALVE INLET TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK36 | MAY10EZ010 | ZK36 | 1560-VT-6381 GEARBOX HORIZONTAL CASING VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK18 | MAY10EZ010 | ZK18 | MAY10EZ910 TURBINE EMERGENCY TRIP | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK17 | MAY10EZ010 | ZK17 | MAY10EZ500 OVERSPEED PROTECTION TRIP | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK16 | MAY10EZ010 | ZK16 | MAY10EK500 OVERSPEED PROTECTION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK15 | MAY10EZ010 | ZK15 | MKY10CE406 TRIPPING COMMAND TURBINE STOP VALVE - COIL 2 | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK14 | MAY10EZ010 | ZK14 | MKY10CE405 TRIPPING COMMAND TURBINE STOP VALVE - COIL 1 | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK28 | MAY10EZ010 | ZK28 | 1560-VT-6294 FRONT END TURBINE Y-AXIS SHAFT VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK29 | MAY10EZ010 | ZK29 | 1560-VT-6295 REAR END TURBINE X-AXIS SHAFT VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM61 | MAY10EZ010 | ZM61 | 1560-TE-6226 STATOR WINDING PHASE W TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40349 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK35 | MAY10EZ010 | ZK35 | 1560-VT-6380 GEARBOX VERTICAL CASING VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK55 | MAY10EZ010 | ZK55 | 1560-TE-6222 STATOR WINDING PHASE U TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK41 | MAY10EZ010 | ZK41 | 1560-VT-6382 TURBINE END GENERATOR VERTICAL BEARING VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK47 | MAY10EZ010 | ZK47 | 1560-ZT-6290 FRONT END TURBINE AXIAL SHAFT POSITION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK49 | MAY10EZ010 | ZK49 | MAX40AA910 TRIP ACTIVATING SOLENOID VALVES | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK50 | MAY10EZ010 | ZK50 | MAY10EZ100 TRIP BY OPERATOR STATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK51 | MAY10EZ010 | ZK51 | MAA10EC010 FG TURBINE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK52 | MAY10EZ010 | ZK52 | MAY10EZ920 GOVERNOR TRIP LOGIC | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK53 | MAY10EZ010 | ZK53 | MAY10EZ990 HP CONTROL VALVES CLOSED POS. ON TURBINE SPEED | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK30 | MAY10EZ010 | ZK30 | 1560-VT-6296 REAR END TURBINE Y-AXIS SHAFT VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM49 | MAY10EZ010 | ZM49 | MAX40AA910 TRIP ACTIVATING SOLENOID VALVES | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK05 | MAY10EZ010 | ZK05 | 1560-TE-6232 EXHAUST STEAM TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM21 | MAY10EZ010 | ZM21 | MAY10CH230 TURBINE EMERGENCY STOP (TCC) | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM26 | MAY10EZ010 | ZM26 | MAY10EK300 EXTERNAL TRIP | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM27 | MAY10EZ010 | ZM27 | 1560-VT-6293 FRONT END TURBINE X-AXIS SHAFT VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM28 | MAY10EZ010 | ZM28 | 1560-VT-6294 FRONT END TURBINE Y-AXIS SHAFT VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40350 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM29 | MAY10EZ010 | ZM29 | 1560-VT-6295 REAR END TURBINE X-AXIS SHAFT VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM30 | MAY10EZ010 | ZM30 | 1560-VT-6296 REAR END TURBINE Y-AXIS SHAFT VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM35 | MAY10EZ010 | ZM35 | 1560-VT-6380 GEARBOX VERTICAL CASING VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM36 | MAY10EZ010 | ZM36 | 1560-VT-6381 GEARBOX HORIZONTAL CASING VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM41 | MAY10EZ010 | ZM41 | 1560-VT-6382 TURBINE END GENERATOR VERTICAL BEARING VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM19 | MAY10EZ010 | ZM19 | MAY10CH210 TURBINE EMERGENCY STOP (TURBINE HALL) | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM47 | MAY10EZ010 | ZM47 | 1560-ZT-6290 FRONT END TURBINE AXIAL SHAFT POSITION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM18 | MAY10EZ010 | ZM18 | MAY10EZ910 TURBINE EMERGENCY TRIP | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM50 | MAY10EZ010 | ZM50 | MAY10EZ100 TRIP BY OPERATOR STATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM51 | MAY10EZ010 | ZM51 | MAA10EC010 FG TURBINE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM52 | MAY10EZ010 | ZM52 | MAY10EZ920 GOVERNOR TRIP LOGIC | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM53 | MAY10EZ010 | ZM53 | MAY10EZ990 HP CONTROL VALVES CLOSED POS. ON TURBINE SPEED | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM55 | MAY10EZ010 | ZM55 | 1560-TE-6222 STATOR WINDING PHASE U TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM56 | MAY10EZ010 | ZM56 | 1560-TE-6223 STATOR WINDING PHASE U TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM57 | MAY10EZ010 | ZM57 | 1560-TE-6228 STATOR WINDING PHASE U TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM58 | MAY10EZ010 | ZM58 | 1560-TE-6224 STATOR WINDING PHASE V TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40351 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM59 | MAY10EZ010 | ZM59 | 1560-TE-6225 STATOR WINDING PHASE V TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM60 | MAY10EZ010 | ZM60 | 1560-TE-6229 STATOR WINDING PHASE V TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM45 | MAY10EZ010 | ZM45 | 1560-VT-6383 EXCITER END GENERATOR VERTICAL BEARING VIBRATION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM62 | MAY10EZ010 | ZM62 | 1560-TE-6227 STATOR WINDING PHASE W TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK69 | MAY10EZ010 | ZK69 | MAY10CE215 FIRE PROTECTION | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK03 | MAY10EZ010 | ZK03 | 1560-TE-6237 LUBE OIL TEMPERATURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK02 | MAY10EZ010 | ZK02 | 1560-PIT-6325 LUBE OIL PRESSURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK01 | MAY10EZ010 | ZK01 | 1560-PIT-6312 TRIP OIL PRESSURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM69 | MAY10EZ010 | ZM69 | MAY10CE215 FIRE PROTECTION | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM68 | MAY10EZ010 | ZM68 | 1560-LI-6278 DRAIN TANK LEVEL | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK20 | MAY10EZ010 | ZK20 | MAY10CH220 TURBINE EMERGENCY STOP (CONTROL ROOM) | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK21 | MAY10EZ010 | ZK21 | MAY10CH230 TURBINE EMERGENCY STOP (TCC) | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM67 | MAY10EZ010 | ZM67 | 1560-TI-6256 EMERGENCY STOP VALVE INLET TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM20 | MAY10EZ010 | ZM20 | MAY10CH220 TURBINE EMERGENCY STOP (CONTROL ROOM) | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZM63 | MAY10EZ010 | ZM63 | 1560-TE-6230 STATOR WINDING PHASE W TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ010 | ZK04 | MAY10EZ010 | ZK04 | 1560-PIT-6317 EXHAUST STEAM PRESSURE | ACTIVE TRIP |  | Signal | 1 | bin | 0 |  |  |  |  | PLC only |  | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 40352 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XQ60 | MAA15CT060 | XQ60 | CASING WALL LOWER HALF TEMPERATURE | - | Monitoring | Signal | 32 | 1112 | °F | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40355 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XQ61 | MAA15CT060 | XQ61 | CASING WALL LOWER HALF TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40357 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XM20 | MAA15CT060 | XM20 | CASING WALL LOWER HALF TEMPERATURE | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40357 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XH54 | MAA15CT060 | XH54 | CASING WALL LOWER HALF TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40357 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XH52 | MAA15CT060 | XH52 | CASING WALL LOWER HALF TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40357 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XH01 | MAA15CT060 | XH01 | CASING WALL LOWER HALF TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40357 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6254 | XH03 | MAA15CT060 | XH03 | CASING WALL LOWER HALF TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40357 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XQ60 | LBB10CT010 | XQ60 | ADMISSION STEAM INLET TEMPERATURE | - |  | Signal | 32 | 752 | °F | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40359 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XQ61 | LBB10CT010 | XQ61 | ADMISSION STEAM INLET TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40361 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XM20 | LBB10CT010 | XM20 | ADMISSION STEAM INLET TEMPERATURE | - |  | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40361 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XH54 | LBB10CT010 | XH54 | ADMISSION STEAM INLET TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40361 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XH52 | LBB10CT010 | XH52 | ADMISSION STEAM INLET TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | calc |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40361 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XH01 | LBB10CT010 | XH01 | ADMISSION STEAM INLET TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | calc |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40361 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6255 | XH03 | LBB10CT010 | XH03 | ADMISSION STEAM INLET TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40361 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XQ60 | MAV10CT010 | XQ60 | LUBE OIL TANK TEMPERATURE | - | Oil | Signal | 32 | 212 | °F | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40363 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XQ61 | MAV10CT010 | XQ61 | LUBE OIL TANK TEMPERATURE | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40365 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XM20 | MAV10CT010 | XM20 | LUBE OIL TANK TEMPERATURE | - | Oil | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40365 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XH54 | MAV10CT010 | XH54 | LUBE OIL TANK TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40365 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XH52 | MAV10CT010 | XH52 | LUBE OIL TANK TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40365 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XH01 | MAV10CT010 | XH01 | LUBE OIL TANK TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40365 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6261 | XH03 | MAV10CT010 | XH03 | LUBE OIL TANK TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40365 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XQ60 | MAK10CY910 | XQ60 | GEARBOX ACCELERATION VERTICAL | - | Monitoring | Signal | 0 | 1312 | ft/s² | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40367 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XQ61 | MAK10CY910 | XQ61 | GEARBOX ACCELERATION VERTICAL | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40369 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XM20 | MAK10CY910 | XM20 | GEARBOX ACCELERATION VERTICAL | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40369 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XH54 | MAK10CY910 | XH54 | GEARBOX ACCELERATION VERTICAL | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40369 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XH52 | MAK10CY910 | XH52 | GEARBOX ACCELERATION VERTICAL | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40369 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XH01 | MAK10CY910 | XH01 | GEARBOX ACCELERATION VERTICAL | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 590 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40369 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VIT-6419 | XH03 | MAK10CY910 | XH03 | GEARBOX ACCELERATION VERTICAL | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40369 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XQ60 | MAK10CY920 | XQ60 | GEARBOX ACCELERATION HORIZONTAL | - | Monitoring | Signal | 0 | 1312 | ft/s² | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40371 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XQ61 | MAK10CY920 | XQ61 | GEARBOX ACCELERATION HORIZONTAL | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40373 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XM20 | MAK10CY920 | XM20 | GEARBOX ACCELERATION HORIZONTAL | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40373 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XH54 | MAK10CY920 | XH54 | GEARBOX ACCELERATION HORIZONTAL | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40373 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XH52 | MAK10CY920 | XH52 | GEARBOX ACCELERATION HORIZONTAL | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40373 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XH01 | MAK10CY920 | XH01 | GEARBOX ACCELERATION HORIZONTAL | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 590 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40373 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VIT-6420 | XH03 | MAK10CY920 | XH03 | GEARBOX ACCELERATION HORIZONTAL | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40373 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XQ60 | MAD10CY011 | XQ60 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Signal | 0 | 7.87 | mils | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40375 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XQ61 | MAD10CY011 | XQ61 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40377 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XM20 | MAD10CY011 | XM20 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40377 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XH54 | MAD10CY011 | XH54 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40377 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XH52 | MAD10CY011 | XH52 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40377 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XH01 | MAD10CY011 | XH01 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 3.27 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40377 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6293 | XH03 | MAD10CY011 | XH03 | FRONT END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 4.26 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40377 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XQ60 | MAD10CY012 | XQ60 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Signal | 0 | 7.87 | mils | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40379 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XQ61 | MAD10CY012 | XQ61 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40381 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XM20 | MAD10CY012 | XM20 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40381 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XH54 | MAD10CY012 | XH54 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40381 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XH52 | MAD10CY012 | XH52 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40381 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XH01 | MAD10CY012 | XH01 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 3.27 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40381 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6294 | XH03 | MAD10CY012 | XH03 | FRONT END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 4.26 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40381 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XQ60 | MAD20CY011 | XQ60 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Signal | 0 | 7.87 | mils | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40383 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XQ61 | MAD20CY011 | XQ61 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40385 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XM20 | MAD20CY011 | XM20 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40385 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XH54 | MAD20CY011 | XH54 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40385 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XH52 | MAD20CY011 | XH52 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40385 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XH01 | MAD20CY011 | XH01 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 3.27 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40385 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6295 | XH03 | MAD20CY011 | XH03 | REAR END TURBINE X-AXIS SHAFT VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 4.26 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40385 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XQ60 | MAD20CY012 | XQ60 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Signal | 0 | 7.87 | mils | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40387 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XQ61 | MAD20CY012 | XQ61 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40389 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XM20 | MAD20CY012 | XM20 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40389 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XH54 | MAD20CY012 | XH54 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40389 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XH52 | MAD20CY012 | XH52 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40389 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XH01 | MAD20CY012 | XH01 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 3.27 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40389 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6296 | XH03 | MAD20CY012 | XH03 | REAR END TURBINE Y-AXIS SHAFT VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 4.26 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40389 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XQ60 | MAK10CY010 | XQ60 | GEARBOX VERTICAL CASING VIBRATION | - | Monitoring | Signal | 0 | 1 | in/s | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40391 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XQ61 | MAK10CY010 | XQ61 | GEARBOX VERTICAL CASING VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40393 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XM20 | MAK10CY010 | XM20 | GEARBOX VERTICAL CASING VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40393 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XH54 | MAK10CY010 | XH54 | GEARBOX VERTICAL CASING VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40393 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XH52 | MAK10CY010 | XH52 | GEARBOX VERTICAL CASING VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40393 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XH01 | MAK10CY010 | XH01 | GEARBOX VERTICAL CASING VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 0.2 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40393 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6380 | XH03 | MAK10CY010 | XH03 | GEARBOX VERTICAL CASING VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 0.39 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40393 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XQ60 | MAK10CY020 | XQ60 | GEARBOX HORIZONTAL CASING VIBRATION | - | Monitoring | Signal | 0 | 1 | in/s | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40395 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XQ61 | MAK10CY020 | XQ61 | GEARBOX HORIZONTAL CASING VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40397 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XM20 | MAK10CY020 | XM20 | GEARBOX HORIZONTAL CASING VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40397 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XH54 | MAK10CY020 | XH54 | GEARBOX HORIZONTAL CASING VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40397 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XH52 | MAK10CY020 | XH52 | GEARBOX HORIZONTAL CASING VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40397 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XH01 | MAK10CY020 | XH01 | GEARBOX HORIZONTAL CASING VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 0.2 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40397 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6381 | XH03 | MAK10CY020 | XH03 | GEARBOX HORIZONTAL CASING VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 0.39 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40397 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XQ60 | MKD10CY020 | XQ60 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Signal | 0 | 1 | in/s | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40399 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XQ61 | MKD10CY020 | XQ61 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40401 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XM20 | MKD10CY020 | XM20 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40401 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XH54 | MKD10CY020 | XH54 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40401 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XH52 | MKD10CY020 | XH52 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40401 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XH01 | MKD10CY020 | XH01 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 0.28 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40401 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-VT-6382 | XH03 | MKD10CY020 | XH03 | TURBINE END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 0.43 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40401 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XQ60 | MKD20CY020 | XQ60 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Signal | 0 | 1 | in/s | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40403 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XQ61 | MKD20CY020 | XQ61 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40405 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XM20 | MKD20CY020 | XM20 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40405 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XH54 | MKD20CY020 | XH54 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40405 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XH52 | MKD20CY020 | XH52 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40405 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XH01 | MKD20CY020 | XH01 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 0.28 |  |  |  | SINGLE ANALOG MEASUREMENT | Warning |  |  |  | SINGLE ANALOG MEASUREMENT | 40405 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-VT-6383 | XH03 | MKD20CY020 | XH03 | EXCITER END GENERATOR HORIZONTAL BEARING VIBRATION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 0.43 |  |  | SINGLE ANALOG MEASUREMENT | Alarm |  |  |  | SINGLE ANALOG MEASUREMENT | 40405 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XQ60 | LCE20CG010 | XQ60 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT | Control | Signal | 0 | 100 | % | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40407 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XQ61 | LCE20CG010 | XQ61 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40409 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XM20 | LCE20CG010 | XM20 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT | Control | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40409 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XH54 | LCE20CG010 | XH54 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40409 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XH52 | LCE20CG010 | XH52 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40409 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XH01 | LCE20CG010 | XH01 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40409 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6522 | XH03 | LCE20CG010 | XH03 | SEAL STEAM CONDENSATE INJECTION CV POSITION | VALVE LIFT |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40409 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XQ60 | MAW20CG010 | XQ60 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT | Control | Signal | 0 | 100 | % | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40411 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XQ61 | MAW20CG010 | XQ61 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40413 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XM20 | MAW20CG010 | XM20 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT | Control | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40413 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XH54 | MAW20CG010 | XH54 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40413 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XH52 | MAW20CG010 | XH52 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40413 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XH01 | MAW20CG010 | XH01 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40413 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZY-6265 | XH03 | MAW20CG010 | XH03 | SEAL STEAM CONTROL VALVE POSITION | VALVE LIFT |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40413 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XQ60 | LBD10CG010 | XQ60 | EXTRACTION STEAM NON RETURN VALVE POSITION | - | Control | Signal | 0 | 100 | % | [6 empty] | SINGLE ANALOG MEASUREMENT | Signal |  |  |  | SINGLE ANALOG MEASUREMENT | 40415 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XQ61 | LBD10CG010 | XQ61 | EXTRACTION STEAM NON RETURN VALVE POSITION | - |  | Status | [9 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40417 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XM20 | LBD10CG010 | XM20 | EXTRACTION STEAM NON RETURN VALVE POSITION | - | Control | Fault | 1 | bin | 0 | [6 empty] | SINGLE ANALOG MEASUREMENT | Fault |  |  |  | SINGLE ANALOG MEASUREMENT | 40417 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XH54 | LBD10CG010 | XH54 | EXTRACTION STEAM NON RETURN VALVE POSITION | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40417 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XH52 | LBD10CG010 | XH52 | EXTRACTION STEAM NON RETURN VALVE POSITION | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40417 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XH01 | LBD10CG010 | XH01 | EXTRACTION STEAM NON RETURN VALVE POSITION | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40417 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD10CG010 | XH03 | LBD10CG010 | XH03 | EXTRACTION STEAM NON RETURN VALVE POSITION | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | SINGLE ANALOG MEASUREMENT |  |  |  |  | SINGLE ANALOG MEASUREMENT | 40417 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XQ60 | MAV10CL910 | XQ60 | LUBE OIL TANK LEVEL | - | Oil | 2oo3 value | -19.92 | 7.64 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41005 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XQ71 | MAV10CL910 | XQ71 | LUBE OIL TANK LEVEL | - | Oil | Single value 1 | -19.92 | 7.64 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41007 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XQ72 | MAV10CL910 | XQ72 | LUBE OIL TANK LEVEL | - | Oil | Single value 2 | -19.92 | 7.64 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41009 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XQ73 | MAV10CL910 | XQ73 | LUBE OIL TANK LEVEL | - | Oil | Single value 3 | -19.92 | 7.64 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41011 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XQ61 | MAV10CL910 | XQ61 | LUBE OIL TANK LEVEL | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XM38 | MAV10CL910 | XM38 | LUBE OIL TANK LEVEL | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XH54 | MAV10CL910 | XH54 | LUBE OIL TANK LEVEL | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XH52 | MAV10CL910 | XH52 | LUBE OIL TANK LEVEL | - | Oil | Warning low | 1 | bin | 0 |  | -1.38 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XH01 | MAV10CL910 | XH01 | LUBE OIL TANK LEVEL | - | Oil | Warning high | 1 | bin | 0 |  |  | 1.42 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XH03 | MAV10CL910 | XH03 | LUBE OIL TANK LEVEL | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XM31 | MAV10CL910 | XM31 | LUBE OIL TANK LEVEL | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XM32 | MAV10CL910 | XM32 | LUBE OIL TANK LEVEL | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-LI-6262 | XM33 | MAV10CL910 | XM33 | LUBE OIL TANK LEVEL | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41013 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XQ60 | MAL20CL910 | XQ60 | DRAIN TANK LEVEL | - |  | 2oo3 value | -21.26 | 31.89 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41025 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XQ71 | MAL20CL910 | XQ71 | DRAIN TANK LEVEL | - |  | Single value 1 | -21.26 | 31.89 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41027 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XQ72 | MAL20CL910 | XQ72 | DRAIN TANK LEVEL | - |  | Single value 2 | -21.26 | 31.89 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41029 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XQ73 | MAL20CL910 | XQ73 | DRAIN TANK LEVEL | - |  | Single value 3 | -21.26 | 31.89 | in | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41031 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XQ61 | MAL20CL910 | XQ61 | DRAIN TANK LEVEL | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XM38 | MAL20CL910 | XM38 | DRAIN TANK LEVEL | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XH54 | MAL20CL910 | XH54 | DRAIN TANK LEVEL | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XH52 | MAL20CL910 | XH52 | DRAIN TANK LEVEL | - |  | Warning low | 1 | bin | 0 |  | 0 |  |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XH01 | MAL20CL910 | XH01 | DRAIN TANK LEVEL | - |  | Warning high | 1 | bin | 0 |  |  | 13.78 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XH03 | MAL20CL910 | XH03 | DRAIN TANK LEVEL | - |  | Alarm high | 1 | bin | 0 |  |  |  | 19.69 |  |  | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XM31 | MAL20CL910 | XM31 | DRAIN TANK LEVEL | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XM32 | MAL20CL910 | XM32 | DRAIN TANK LEVEL | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-LI-6278 | XM33 | MAL20CL910 | XM33 | DRAIN TANK LEVEL | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41033 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XQ60 | LBA10CP920 | XQ60 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | 2oo3 value | 0 | 1450 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41035 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XQ71 | LBA10CP920 | XQ71 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Single value 1 | 0 | 1450 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41037 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XQ72 | LBA10CP920 | XQ72 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Single value 2 | 0 | 1450 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41039 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XQ73 | LBA10CP920 | XQ73 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Single value 3 | 0 | 1450 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41041 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XQ61 | LBA10CP920 | XQ61 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XM38 | LBA10CP920 | XM38 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XH54 | LBA10CP920 | XH54 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XH52 | LBA10CP920 | XH52 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Warning low | 1 | bin | 0 |  | 825.8 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XH01 | LBA10CP920 | XH01 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | 914.5 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XH03 | LBA10CP920 | XH03 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XM31 | LBA10CP920 | XM31 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XM32 | LBA10CP920 | XM32 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PI-6321 | XM33 | LBA10CP920 | XM33 | EMERGENCY STOP VALVE INLET PRESSURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41043 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XQ60 | MAX40CP920 | XQ60 | TRIP OIL PRESSURE | - | Oil | 2oo3 value | 0 | 3625 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41045 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XQ71 | MAX40CP920 | XQ71 | TRIP OIL PRESSURE | - | Oil | Single value 1 | 0 | 3625 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41047 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XQ72 | MAX40CP920 | XQ72 | TRIP OIL PRESSURE | - | Oil | Single value 2 | 0 | 3625 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41049 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XQ73 | MAX40CP920 | XQ73 | TRIP OIL PRESSURE | - | Oil | Single value 3 | 0 | 3625 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41051 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XQ61 | MAX40CP920 | XQ61 | TRIP OIL PRESSURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XM38 | MAX40CP920 | XM38 | TRIP OIL PRESSURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XH54 | MAX40CP920 | XH54 | TRIP OIL PRESSURE | - | Oil | Alarm low | 1 | bin | 0 | 1305 | [5 empty] | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XH52 | MAX40CP920 | XH52 | TRIP OIL PRESSURE | - | Oil | Warning low | 1 | bin | 0 |  | 1450 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XH01 | MAX40CP920 | XH01 | TRIP OIL PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XH03 | MAX40CP920 | XH03 | TRIP OIL PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XM31 | MAX40CP920 | XM31 | TRIP OIL PRESSURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XM32 | MAX40CP920 | XM32 | TRIP OIL PRESSURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6312 | XM33 | MAX40CP920 | XM33 | TRIP OIL PRESSURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41053 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XQ60 | MAC10CP950 | XQ60 | EXHAUST STEAM PRESSURE | - |  | 2oo3 value | 0 | 23.2 | psi(a) | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41055 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XQ71 | MAC10CP950 | XQ71 | EXHAUST STEAM PRESSURE | - |  | Single value 1 | 0 | 23.2 | psi(a) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41057 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XQ72 | MAC10CP950 | XQ72 | EXHAUST STEAM PRESSURE | - |  | Single value 2 | 0 | 23.2 | psi(a) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41059 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XQ73 | MAC10CP950 | XQ73 | EXHAUST STEAM PRESSURE | - |  | Single value 3 | 0 | 23.2 | psi(a) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41061 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XQ61 | MAC10CP950 | XQ61 | EXHAUST STEAM PRESSURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XM38 | MAC10CP950 | XM38 | EXHAUST STEAM PRESSURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XH54 | MAC10CP950 | XH54 | EXHAUST STEAM PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XH52 | MAC10CP950 | XH52 | EXHAUST STEAM PRESSURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XH01 | MAC10CP950 | XH01 | EXHAUST STEAM PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | calc |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XH03 | MAC10CP950 | XH03 | EXHAUST STEAM PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | calc |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XM31 | MAC10CP950 | XM31 | EXHAUST STEAM PRESSURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XM32 | MAC10CP950 | XM32 | EXHAUST STEAM PRESSURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6317 | XM33 | MAC10CP950 | XM33 | EXHAUST STEAM PRESSURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41063 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XQ60 | MAV40CP910 | XQ60 | LUBE OIL PRESSURE | - | Oil | 2oo3 value | 0 | 58 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41065 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XQ71 | MAV40CP910 | XQ71 | LUBE OIL PRESSURE | - | Oil | Single value 1 | 0 | 58 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41067 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XQ72 | MAV40CP910 | XQ72 | LUBE OIL PRESSURE | - | Oil | Single value 2 | 0 | 58 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41069 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XQ73 | MAV40CP910 | XQ73 | LUBE OIL PRESSURE | - | Oil | Single value 3 | 0 | 58 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41071 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XQ61 | MAV40CP910 | XQ61 | LUBE OIL PRESSURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XM38 | MAV40CP910 | XM38 | LUBE OIL PRESSURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XH54 | MAV40CP910 | XH54 | LUBE OIL PRESSURE | - | Oil | Alarm low | 1 | bin | 0 | 14.5 | [5 empty] | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XH52 | MAV40CP910 | XH52 | LUBE OIL PRESSURE | - | Oil | Warning low | 1 | bin | 0 |  | 24.66 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XH01 | MAV40CP910 | XH01 | LUBE OIL PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XH03 | MAV40CP910 | XH03 | LUBE OIL PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XM31 | MAV40CP910 | XM31 | LUBE OIL PRESSURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XM32 | MAV40CP910 | XM32 | LUBE OIL PRESSURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PIT-6325 | XM33 | MAV40CP910 | XM33 | LUBE OIL PRESSURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41073 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XQ60 | MAA10CP920 | XQ60 | HP STAGE GROUP INLET PRESSURE | - |  | 2oo3 value | -12.18 | 857.8 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41075 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XQ71 | MAA10CP920 | XQ71 | HP STAGE GROUP INLET PRESSURE | - |  | Single value 1 | -12.18 | 857.8 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41077 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XQ72 | MAA10CP920 | XQ72 | HP STAGE GROUP INLET PRESSURE | - |  | Single value 2 | -12.18 | 857.8 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41079 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XQ73 | MAA10CP920 | XQ73 | HP STAGE GROUP INLET PRESSURE | - |  | Single value 3 | -12.18 | 857.8 | psi(g) | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41081 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XQ61 | MAA10CP920 | XQ61 | HP STAGE GROUP INLET PRESSURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XM38 | MAA10CP920 | XM38 | HP STAGE GROUP INLET PRESSURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XH54 | MAA10CP920 | XH54 | HP STAGE GROUP INLET PRESSURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XH52 | MAA10CP920 | XH52 | HP STAGE GROUP INLET PRESSURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XH01 | MAA10CP920 | XH01 | HP STAGE GROUP INLET PRESSURE | - |  | Warning high | 1 | bin | 0 |  |  | - |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XH03 | MAA10CP920 | XH03 | HP STAGE GROUP INLET PRESSURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XM31 | MAA10CP920 | XM31 | HP STAGE GROUP INLET PRESSURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XM32 | MAA10CP920 | XM32 | HP STAGE GROUP INLET PRESSURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6330 | XM33 | MAA10CP920 | XM33 | HP STAGE GROUP INLET PRESSURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41083 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XQ60 | MAC10CT950 | XQ60 | EXHAUST STEAM TEMPERATURE | - |  | 2oo3 value | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41085 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XQ71 | MAC10CT950 | XQ71 | EXHAUST STEAM TEMPERATURE | - |  | Single value 1 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41087 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XQ72 | MAC10CT950 | XQ72 | EXHAUST STEAM TEMPERATURE | - |  | Single value 2 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41089 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XQ73 | MAC10CT950 | XQ73 | EXHAUST STEAM TEMPERATURE | - |  | Single value 3 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41091 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XQ61 | MAC10CT950 | XQ61 | EXHAUST STEAM TEMPERATURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XM38 | MAC10CT950 | XM38 | EXHAUST STEAM TEMPERATURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XH54 | MAC10CT950 | XH54 | EXHAUST STEAM TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XH52 | MAC10CT950 | XH52 | EXHAUST STEAM TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XH01 | MAC10CT950 | XH01 | EXHAUST STEAM TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 194 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XH03 | MAC10CT950 | XH03 | EXHAUST STEAM TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | 230 |  |  | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XM31 | MAC10CT950 | XM31 | EXHAUST STEAM TEMPERATURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XM32 | MAC10CT950 | XM32 | EXHAUST STEAM TEMPERATURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6232 | XM33 | MAC10CT950 | XM33 | EXHAUST STEAM TEMPERATURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41093 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XQ60 | MAV40CT910 | XQ60 | LUBE OIL TEMPERATURE | - | Oil | 2oo3 value | 32 | 212 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41095 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XQ71 | MAV40CT910 | XQ71 | LUBE OIL TEMPERATURE | - | Oil | Single value 1 | 32 | 212 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41097 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XQ72 | MAV40CT910 | XQ72 | LUBE OIL TEMPERATURE | - | Oil | Single value 2 | 32 | 212 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41099 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XQ73 | MAV40CT910 | XQ73 | LUBE OIL TEMPERATURE | - | Oil | Single value 3 | 32 | 212 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41101 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XQ61 | MAV40CT910 | XQ61 | LUBE OIL TEMPERATURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XM38 | MAV40CT910 | XM38 | LUBE OIL TEMPERATURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XH54 | MAV40CT910 | XH54 | LUBE OIL TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XH52 | MAV40CT910 | XH52 | LUBE OIL TEMPERATURE | - | Oil | Warning low | 1 | bin | 0 |  | 95 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XH01 | MAV40CT910 | XH01 | LUBE OIL TEMPERATURE | - | Oil | Warning high | 1 | bin | 0 |  |  | 131 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XH03 | MAV40CT910 | XH03 | LUBE OIL TEMPERATURE | - | Oil | Alarm high | 1 | bin | 0 |  |  |  | 149 |  |  | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XM31 | MAV40CT910 | XM31 | LUBE OIL TEMPERATURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XM32 | MAV40CT910 | XM32 | LUBE OIL TEMPERATURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6237 | XM33 | MAV40CT910 | XM33 | LUBE OIL TEMPERATURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41103 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XQ60 | MKA10CT950 | XQ60 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | 2oo3 value | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41105 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XQ71 | MKA10CT950 | XQ71 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Single value 1 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41107 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XQ72 | MKA10CT950 | XQ72 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Single value 2 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41109 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XQ73 | MKA10CT950 | XQ73 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Single value 3 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41111 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XQ61 | MKA10CT950 | XQ61 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XM38 | MKA10CT950 | XM38 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XH54 | MKA10CT950 | XH54 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XH52 | MKA10CT950 | XH52 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XH01 | MKA10CT950 | XH01 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 122 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XH03 | MKA10CT950 | XH03 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XM31 | MKA10CT950 | XM31 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XM32 | MKA10CT950 | XM32 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TE-6240 | XM33 | MKA10CT950 | XM33 | TURBINE END GENERATOR COLD AIR TEMPERATURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41113 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XQ60 | MKA10CT955 | XQ60 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | 2oo3 value | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41115 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XQ71 | MKA10CT955 | XQ71 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Single value 1 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41117 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XQ72 | MKA10CT955 | XQ72 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Single value 2 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41119 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XQ73 | MKA10CT955 | XQ73 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Single value 3 | 32 | 392 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41121 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XQ61 | MKA10CT955 | XQ61 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XM38 | MKA10CT955 | XM38 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XH54 | MKA10CT955 | XH54 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | - | [5 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XH52 | MKA10CT955 | XH52 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | - |  |  |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XH01 | MKA10CT955 | XH01 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 122 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XH03 | MKA10CT955 | XH03 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XM31 | MKA10CT955 | XM31 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XM32 | MKA10CT955 | XM32 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TE-6241 | XM33 | MKA10CT955 | XM33 | EXCITER END GENERATOR COLD AIR TEMPERATURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41123 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XQ60 | LBA10CT920 | XQ60 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | 2oo3 value | 32 | 1112 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41125 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XQ71 | LBA10CT920 | XQ71 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Single value 1 | 32 | 1112 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41127 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XQ72 | LBA10CT920 | XQ72 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Single value 2 | 32 | 1112 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41129 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XQ73 | LBA10CT920 | XQ73 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Single value 3 | 32 | 1112 | °F | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41131 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XQ61 | LBA10CT920 | XQ61 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XM38 | LBA10CT920 | XM38 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XH54 | LBA10CT920 | XH54 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Alarm low | 1 | bin | 0 | 751.4 | [5 empty] | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XH52 | LBA10CT920 | XH52 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Warning low | 1 | bin | 0 |  | 885.6 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XH01 | LBA10CT920 | XH01 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Warning high | 1 | bin | 0 |  |  | 914.4 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XH03 | LBA10CT920 | XH03 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Alarm high | 1 | bin | 0 |  |  |  | - |  |  | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XM31 | LBA10CT920 | XM31 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XM32 | LBA10CT920 | XM32 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TI-6256 | XM33 | LBA10CT920 | XM33 | EMERGENCY STOP VALVE INLET TEMPERATURE | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41133 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XQ60 | MAD10CG910 | XQ60 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | 2oo3 value | -39.37 | 39.37 | mils | [6 empty] | 2oo3 ANALOG MEASUREMENT | 2oo3 |  |  |  | 2oo3 ANALOG MEASUREMENT | 41135 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XQ71 | MAD10CG910 | XQ71 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Single value 1 | -39.37 | 39.37 | mils | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41137 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XQ72 | MAD10CG910 | XQ72 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Single value 2 | -39.37 | 39.37 | mils | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41139 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XQ73 | MAD10CG910 | XQ73 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Single value 3 | -39.37 | 39.37 | mils | [6 empty] | 2oo3 ANALOG MEASUREMENT | Single |  |  |  | 2oo3 ANALOG MEASUREMENT | 41141 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XQ61 | MAD10CG910 | XQ61 | FRONT END TURBINE AXIAL SHAFT POSITION | - |  | Status | [9 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XM38 | MAD10CG910 | XM38 | FRONT END TURBINE AXIAL SHAFT POSITION | - |  | Fault 2oo3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XH54 | MAD10CG910 | XH54 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Alarm low | 1 | bin | 0 | -23.62 | [5 empty] | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XH52 | MAD10CG910 | XH52 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Warning low | 1 | bin | 0 |  | -15.75 |  |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XH01 | MAD10CG910 | XH01 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Warning high | 1 | bin | 0 |  |  | 15.75 |  |  |  | 2oo3 ANALOG MEASUREMENT | Warning |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XH03 | MAD10CG910 | XH03 | FRONT END TURBINE AXIAL SHAFT POSITION | - | Monitoring | Alarm high | 1 | bin | 0 |  |  |  | 23.62 |  |  | 2oo3 ANALOG MEASUREMENT | Alarm |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XM31 | MAD10CG910 | XM31 | FRONT END TURBINE AXIAL SHAFT POSITION | - |  | Fault value 1 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XM32 | MAD10CG910 | XM32 | FRONT END TURBINE AXIAL SHAFT POSITION | - |  | Fault value 2 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-ZT-6290 | XM33 | MAD10CG910 | XM33 | FRONT END TURBINE AXIAL SHAFT POSITION | - |  | Fault value 3 | 1 | bin | 0 | [6 empty] | 2oo3 ANALOG MEASUREMENT |  |  |  |  | 2oo3 ANALOG MEASUREMENT | 41143 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ43 | MAY10EU500 | YQ43 | KEY PERFORMANCE INDICATOR (KPI) | STOP HOURS |  | Signal | 0 | 350400 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41345 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ42 | MAY10EU500 | YQ42 | KEY PERFORMANCE INDICATOR (KPI) | OPERATING HOURS (OH) |  | Signal | 0 | 350400 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41347 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ39 | MAY10EU500 | YQ39 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENT OPERATING HOURS (EOH) |  | Signal | 0 | 1010400 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41349 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ18 | MAY10EU500 | YQ18 | KEY PERFORMANCE INDICATOR (KPI) | HOT STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41351 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ15 | MAY10EU500 | YQ15 | KEY PERFORMANCE INDICATOR (KPI) | WARM STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41353 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ12 | MAY10EU500 | YQ12 | KEY PERFORMANCE INDICATOR (KPI) | COLD STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41355 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ19 | MAY10EU500 | YQ19 | KEY PERFORMANCE INDICATOR (KPI) | TOTAL STARTS |  | Signal | 0 | 66000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41357 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ33 | MAY10EU500 | YQ33 | KEY PERFORMANCE INDICATOR (KPI) | BACKUP STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41359 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ22 | MAY10EU500 | YQ22 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENT HOT START HOURS (ESH-HOT) |  | Signal | 0 | 660000 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41361 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ36 | MAY10EU500 | YQ36 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENTNORMAL START HOURS (ESH-NORM) |  | Signal | 0 | 660000 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41363 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ21 | MAY10EU500 | YQ21 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENT WARM START HOURS (ESH-WARM) |  | Signal | 0 | 660000 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41365 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ35 | MAY10EU500 | YQ35 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENT ECO START HOURS (ESH-ECO) |  | Signal | 0 | 660000 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41367 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ20 | MAY10EU500 | YQ20 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENT COLD START HOURS (ESH-COLD) |  | Signal | 0 | 660000 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41369 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ34 | MAY10EU500 | YQ34 | KEY PERFORMANCE INDICATOR (KPI) | TOTAL STARTS |  | Signal | 0 | 66000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41371 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ32 | MAY10EU500 | YQ32 | KEY PERFORMANCE INDICATOR (KPI) | FAST STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41373 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ31 | MAY10EU500 | YQ31 | KEY PERFORMANCE INDICATOR (KPI) | NORMAL STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41375 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ30 | MAY10EU500 | YQ30 | KEY PERFORMANCE INDICATOR (KPI) | ECO STARTS |  | Signal | 0 | 22000 | - | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41377 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EU500 | YQ23 | MAY10EU500 | YQ23 | KEY PERFORMANCE INDICATOR (KPI) | EQUIVALENT OPERATING HOURS (EOH) |  | Signal | 0 | 1010400 | hour | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41379 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE061 | XQ01 | MKY10DE061 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE EXCITATION CURRENT | Monitoring | Signal | 0 | 22.8 | A | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41381 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE062 | XQ01 | MKY10DE062 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE EXCITATION VOLTAGE | Monitoring | Signal | -84.6 | 84.6 | V | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41383 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE064 | XQ01 | MKY10DE064 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE GENERATOR VOLTAGE | Monitoring | Signal | 11.04 | 16.56 | kV | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41385 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE066 | XQ01 | MKY10DE066 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE POWER FACTOR GENERATOR |  | Signal | 0,5 cap | 0,5 ind | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 41387 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE068 | XQ01 | MKY10DE068 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE REACTIVE POWER GENERATOR | Monitoring | Signal | -62.22 | 62.22 | MVAr | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41389 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE070 | XQ01 | MKY10DE070 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE POWER FACTOR NET COUPLING POINT |  | Signal | 0,5 cap | 0,5 ind | - | [6 empty] | ANALOG SEND |  |  |  |  | ANALOG SEND | 41391 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE072 | XQ01 | MKY10DE072 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE REACTIVE POWER NET COUPLING POINT | Monitoring | Signal | -62.22 | 62.22 | MVAr | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41393 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE073 | XQ01 | MKY10DE073 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE ACTIVE POWER NET COUPLING POINT | Monitoring | Signal | -62.22 | 62.22 | MW | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41395 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE074 | XQ01 | MKY10DE074 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE ACTIVE POWER GENERATOR | Monitoring | Signal | -62.22 | 62.22 | MW | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41397 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE075 | XQ01 | MKY10DE075 | XQ01 | GENERATOR EXCITATION SYSTEM | ACTUAL VALUE GENERATOR CURRENT | Monitoring | Signal | 0 | 2604 | A | [6 empty] | ANALOG SEND | Signal |  |  |  | ANALOG SEND | 41399 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZK26 | MAY10EZ010 | ZK26 | MAY10EK300 EXTERNAL TRIP | ACTIVE TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZK27 | MAY10EZ010 | ZK27 | 1560-VT-6293 FRONT END TURBINE X-AXIS SHAFT VIBRATION | ACTIVE TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM01 | MAY10EZ010 | ZM01 | 1560-PIT-6312 TRIP OIL PRESSURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM02 | MAY10EZ010 | ZM02 | 1560-PIT-6325 LUBE OIL PRESSURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM03 | MAY10EZ010 | ZM03 | 1560-TE-6237 LUBE OIL TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM04 | MAY10EZ010 | ZM04 | 1560-PIT-6317 EXHAUST STEAM PRESSURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM05 | MAY10EZ010 | ZM05 | 1560-TE-6232 EXHAUST STEAM TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM14 | MAY10EZ010 | ZM14 | MKY10CE405 TRIPPING COMMAND TURBINE STOP VALVE - COIL 1 | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM15 | MAY10EZ010 | ZM15 | MKY10CE406 TRIPPING COMMAND TURBINE STOP VALVE - COIL 2 | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM16 | MAY10EZ010 | ZM16 | MAY10EK500 OVERSPEED PROTECTION | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM17 | MAY10EZ010 | ZM17 | MAY10EZ500 OVERSPEED PROTECTION TRIP | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ010 | ZM64 | MAY10EZ010 | ZM64 | 1560-TIT-6255 ADMISSION STEAM INLET TEMPERATURE | FIRST TRIPPED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ910 | XG01 | MAY10EZ910 | XG01 | MANUAL TRIP | TRIP VOTER 1 |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ920 | ZT12 | MAY10EZ920 | ZT12 | SPEED < MIN AFTER START | ACTIVE TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EZ920 | ZT11 | MAY10EZ920 | ZT11 | N< 100 RPM AND SPEED CTRL OUPUT > 50% | ACTIVE TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE148 | XG01 | MKY10CE148 | XG01 | GENERATOR PROTECTION(F1) | UNDERVOLTAGE << TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41515 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE248 | XG01 | MKY10CE248 | XG01 | GENERATOR PROTECTION(-F2) | UNDERVOLTAGE << TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10CE403 | YB01 | MKY10CE403 | YB01 | REVERSE POWER RELEASING BY TURBINE PROTECTION (SYSTEM A) | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10CE404 | YB01 | MKY10CE404 | YB01 | REVERSE POWER RELEASING BY TURBINE PROTECTION (SYSTEM B) | ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE240 | XA06 | MKY10DE240 | XA06 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE LOWER LIMIT REACHED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE240 | XA05 | MKY10DE240 | XA05 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE UPPER LIMIT REACHED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE245 | XA05 | MKY10DE245 | XA05 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER IS RELEASED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE245 | XA06 | MKY10DE245 | XA06 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE330 | XA05 | MKY10DE330 | XA05 | GENERATOR EXCITATION SYSTEM | EXCITATION IS IN LOCAL CONTROL MODE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE332 | XA05 | MKY10DE332 | XA05 | GENERATOR EXCITATION SYSTEM | EXCITATION IS READY TO START |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE333 | XA14 | MKY10DE333 | XA14 | GENERATOR EXCITATION SYSTEM | OPERATION PARALLEL TO GRID |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE334 | XA14 | MKY10DE334 | XA14 | GENERATOR EXCITATION SYSTEM | EARTHING SWITCH IS CLOSED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE335 | XA05 | MKY10DE335 | XA05 | GENERATOR EXCITATION SYSTEM | GROUP ALARM |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE336 | XA05 | MKY10DE336 | XA05 | GENERATOR EXCITATION SYSTEM | GROUP FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE337 | XA05 | MKY10DE337 | XA05 | GENERATOR EXCITATION SYSTEM | TRIP BY EXCITATION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE338 | XA05 | MKY10DE338 | XA05 | GENERATOR EXCITATION SYSTEM | TRIP BY GENERATOR PROTECTION |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE339A | XA05 | MKY10DE339A | XA05 | GENERATOR EXCITATION SYSTEM (CHANNEL 1) | CHANNEL FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41516 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE339B | XA05 | MKY10DE339B | XA05 | GENERATOR EXCITATION SYSTEM (CHANNEL 2) | CHANNEL FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE340 | XA45 | MKY10DE340 | XA45 | GENERATOR EXCITATION SYSTEM | AUTOMATIC CHANNEL SWITCH-OVER |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE341 | XA45 | MKY10DE341 | XA45 | GENERATOR EXCITATION SYSTEM | EMERGENCY SWITCHOVER TO MANUAL |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE342 | XA05 | MKY10DE342 | XA05 | GENERATOR EXCITATION SYSTEM | DIODE SUPERVISION FAULT DETECTED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE343 | XA05 | MKY10DE343 | XA05 | GENERATOR EXCITATION SYSTEM | OVEREXCITATION LIMITER IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE344 | XA05 | MKY10DE344 | XA05 | GENERATOR EXCITATION SYSTEM | STATOR CURRENT LIMITER IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE345 | XA05 | MKY10DE345 | XA05 | GENERATOR EXCITATION SYSTEM | UNDEREXCITATION LIMITER IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE346 | XA05 | MKY10DE346 | XA05 | GENERATOR EXCITATION SYSTEM | CEILING CURRENT FOR > 10S |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE347 | XA05 | MKY10DE347 | XA05 | GENERATOR EXCITATION SYSTEM | U/F LIMITER IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE348 | XA05 | MKY10DE348 | XA05 | GENERATOR EXCITATION SYSTEM | NO LOAD LIMITER IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE349 | XA05 | MKY10DE349 | XA05 | GENERATOR EXCITATION SYSTEM | EXCITATION FEEDBACK UG>90% |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE350 | XA05 | MKY10DE350 | XA05 | GENERATOR EXCITATION SYSTEM | EXCIT. FEEDBACK Q = ZERO |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE351 | XA51 | MKY10DE351 | XA51 | GENERATOR EXCITATION SYSTEM | CIRCUIT BREAKER TRIP GENERAL |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 12 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE352 | XA51 | MKY10DE352 | XA51 | GENERATOR EXCITATION SYSTEM | VOLTAGE TRANSFORMER PROTECTIVE SWITCH TRIP |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 13 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE353 | XA51 | MKY10DE353 | XA51 | GENERATOR EXCITATION SYSTEM | EXCITATION INTERNAL COMMUNICATION FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 14 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE354 | XA05 | MKY10DE354 | XA05 | GENERATOR EXCITATION SYSTEM | GENERATOR ACTUAL VALUE ACQUISITION FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41517 | 15 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE355 | XA05 | MKY10DE355 | XA05 | GENERATOR EXCITATION SYSTEM | EXCITATION FAULT 24 V DC CIRCUIT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE356 | XA53 | MKY10DE356 | XA53 | GENERATOR EXCITATION SYSTEM | SYNCHRONIZING VOLTAGE THYRISTOR BRIDGE FAULTY |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE356 | XA54 | MKY10DE356 | XA54 | GENERATOR EXCITATION SYSTEM | THYRISTOR FUSE FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE356 | XA52 | MKY10DE356 | XA52 | GENERATOR EXCITATION SYSTEM | OVERTEMPERATURE SINAMICS DC MASTER S120 |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE356 | XA51 | MKY10DE356 | XA51 | GENERATOR EXCITATION SYSTEM | GROUP ALARM SINAMICS DC MASTER S120 |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE357 | XA05 | MKY10DE357 | XA05 | GENERATOR EXCITATION SYSTEM | EXCITATION DC OVERVOLTAGE PROTECTION IS ACTIVE |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE358 | XA05 | MKY10DE358 | XA05 | GENERATOR EXCITATION SYSTEM | CEILING VOLTAGE SUPERVISION HAS ACTIVATED |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE359 | XA05 | MKY10DE359 | XA05 | GENERATOR EXCITATION SYSTEM | ACTIVE POWER LOAD LIMITATION GENERATOR - DEMAND |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10GS010 | XB20 | MKY10GS010 | XB20 | GENERATOR EXCITATION SYSTEM | EXCITATION MAIN CIRCUIT BREAKER RUNTIME FAULT |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10GS010 | XB01 | MKY10GS010 | XB01 | GENERATOR EXCITATION SYSTEM | EXCITATION MAIN CIRCUIT BREAKER IS ON |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10GS010 | XB02 | MKY10GS010 | XB02 | GENERATOR EXCITATION SYSTEM | EXCITATION MAIN CIRCUIT BREAKER IS OFF |  | Signal | 1 | bin | 0 | [6 empty] | SINGLE BINARY MEASUREMENT |  |  |  |  | SINGLE BINARY MEASUREMENT | 41518 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XQ51 | MAY10DE020 | XQ51 | LOAD CONTROLLER | - | Control | Actual set point closed loop | 0 | 35.89 | MW | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41543 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XQ52 | MAY10DE020 | XQ52 | LOAD CONTROLLER | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41545 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC61 | MAY10DE020 | XC61 | LOAD CONTROLLER | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC01 | MAY10DE020 | XC01 | LOAD CONTROLLER | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC02 | MAY10DE020 | XC02 | LOAD CONTROLLER | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC20 | MAY10DE020 | XC20 | LOAD CONTROLLER | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41547 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC81 | MAY10DE020 | XC81 | LOAD CONTROLLER | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC82 | MAY10DE020 | XC82 | LOAD CONTROLLER | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC91 | MAY10DE020 | XC91 | LOAD CONTROLLER | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC92 | MAY10DE020 | XC92 | LOAD CONTROLLER | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | ZB01 | MAY10DE020 | ZB01 | LOAD CONTROLLER | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | ZB02 | MAY10DE020 | ZB02 | LOAD CONTROLLER | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE020 | XC98 | MAY10DE020 | XC98 | LOAD CONTROLLER | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41547 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XQ51 | MAY10DE120 | XQ51 | LOAD LIMIT CONTROLLER | - | Control | Actual set point closed loop | 0 | 35.89 | MW | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41548 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XQ52 | MAY10DE120 | XQ52 | LOAD LIMIT CONTROLLER | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41550 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC61 | MAY10DE120 | XC61 | LOAD LIMIT CONTROLLER | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC01 | MAY10DE120 | XC01 | LOAD LIMIT CONTROLLER | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC02 | MAY10DE120 | XC02 | LOAD LIMIT CONTROLLER | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC20 | MAY10DE120 | XC20 | LOAD LIMIT CONTROLLER | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41552 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC81 | MAY10DE120 | XC81 | LOAD LIMIT CONTROLLER | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC82 | MAY10DE120 | XC82 | LOAD LIMIT CONTROLLER | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC91 | MAY10DE120 | XC91 | LOAD LIMIT CONTROLLER | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC92 | MAY10DE120 | XC92 | LOAD LIMIT CONTROLLER | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | ZB01 | MAY10DE120 | ZB01 | LOAD LIMIT CONTROLLER | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | ZB02 | MAY10DE120 | ZB02 | LOAD LIMIT CONTROLLER | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE120 | XC98 | MAY10DE120 | XC98 | LOAD LIMIT CONTROLLER | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41552 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XQ51 | MAY10DP030 | XQ51 | INLET PRESSURE CONTROLLER | - | Control | Actual set point closed loop | 825.8 | 914.5 | psi(g) | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41553 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XQ52 | MAY10DP030 | XQ52 | INLET PRESSURE CONTROLLER | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41555 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC61 | MAY10DP030 | XC61 | INLET PRESSURE CONTROLLER | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC01 | MAY10DP030 | XC01 | INLET PRESSURE CONTROLLER | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC02 | MAY10DP030 | XC02 | INLET PRESSURE CONTROLLER | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC20 | MAY10DP030 | XC20 | INLET PRESSURE CONTROLLER | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41557 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC81 | MAY10DP030 | XC81 | INLET PRESSURE CONTROLLER | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC82 | MAY10DP030 | XC82 | INLET PRESSURE CONTROLLER | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC91 | MAY10DP030 | XC91 | INLET PRESSURE CONTROLLER | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC92 | MAY10DP030 | XC92 | INLET PRESSURE CONTROLLER | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | ZB01 | MAY10DP030 | ZB01 | INLET PRESSURE CONTROLLER | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | ZB02 | MAY10DP030 | ZB02 | INLET PRESSURE CONTROLLER | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP030 | XC98 | MAY10DP030 | XC98 | INLET PRESSURE CONTROLLER | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41557 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XQ51 | MAY10DP050 | XQ51 | ADMISSION PRESSURE CONTROLLER | - | Control | Actual set point closed loop | 0 | 1 | bin | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41558 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XQ52 | MAY10DP050 | XQ52 | ADMISSION PRESSURE CONTROLLER | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41560 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC61 | MAY10DP050 | XC61 | ADMISSION PRESSURE CONTROLLER | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC01 | MAY10DP050 | XC01 | ADMISSION PRESSURE CONTROLLER | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC02 | MAY10DP050 | XC02 | ADMISSION PRESSURE CONTROLLER | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC20 | MAY10DP050 | XC20 | ADMISSION PRESSURE CONTROLLER | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41562 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC81 | MAY10DP050 | XC81 | ADMISSION PRESSURE CONTROLLER | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC82 | MAY10DP050 | XC82 | ADMISSION PRESSURE CONTROLLER | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC91 | MAY10DP050 | XC91 | ADMISSION PRESSURE CONTROLLER | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC92 | MAY10DP050 | XC92 | ADMISSION PRESSURE CONTROLLER | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | ZB01 | MAY10DP050 | ZB01 | ADMISSION PRESSURE CONTROLLER | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | ZB02 | MAY10DP050 | ZB02 | ADMISSION PRESSURE CONTROLLER | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP050 | XC98 | MAY10DP050 | XC98 | ADMISSION PRESSURE CONTROLLER | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41562 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XQ51 | MAY10DP130 | XQ51 | INLET PRESSURE LIMIT CONTROLLER | - | Control | Actual set point closed loop | 825.8 | 914.5 | psi(g) | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41563 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XQ52 | MAY10DP130 | XQ52 | INLET PRESSURE LIMIT CONTROLLER | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41565 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC61 | MAY10DP130 | XC61 | INLET PRESSURE LIMIT CONTROLLER | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC01 | MAY10DP130 | XC01 | INLET PRESSURE LIMIT CONTROLLER | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC02 | MAY10DP130 | XC02 | INLET PRESSURE LIMIT CONTROLLER | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC20 | MAY10DP130 | XC20 | INLET PRESSURE LIMIT CONTROLLER | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41567 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC81 | MAY10DP130 | XC81 | INLET PRESSURE LIMIT CONTROLLER | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC82 | MAY10DP130 | XC82 | INLET PRESSURE LIMIT CONTROLLER | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC91 | MAY10DP130 | XC91 | INLET PRESSURE LIMIT CONTROLLER | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC92 | MAY10DP130 | XC92 | INLET PRESSURE LIMIT CONTROLLER | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | ZB01 | MAY10DP130 | ZB01 | INLET PRESSURE LIMIT CONTROLLER | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | ZB02 | MAY10DP130 | ZB02 | INLET PRESSURE LIMIT CONTROLLER | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP130 | XC98 | MAY10DP130 | XC98 | INLET PRESSURE LIMIT CONTROLLER | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41567 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XQ51 | MAY10DP210 | XQ51 | EXTRACTION PRESSURE CONTROLLER E1 | - | Control | Actual set point closed loop | 61.79 | 77.74 | psi(g) | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41568 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XQ52 | MAY10DP210 | XQ52 | EXTRACTION PRESSURE CONTROLLER E1 | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41570 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC61 | MAY10DP210 | XC61 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC01 | MAY10DP210 | XC01 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC02 | MAY10DP210 | XC02 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC20 | MAY10DP210 | XC20 | EXTRACTION PRESSURE CONTROLLER E1 | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41572 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC81 | MAY10DP210 | XC81 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC82 | MAY10DP210 | XC82 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC91 | MAY10DP210 | XC91 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC92 | MAY10DP210 | XC92 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | ZB01 | MAY10DP210 | ZB01 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | ZB02 | MAY10DP210 | ZB02 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP210 | XC98 | MAY10DP210 | XC98 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41572 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XQ51 | MAY10DS010 | XQ51 | SPEED CONTROLLER | - | Control | Actual set point closed loop | 0 | 7737 | rpm | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41573 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XQ52 | MAY10DS010 | XQ52 | SPEED CONTROLLER | - | Control | Actual set point open loop | 0 | 100 | % | [6 empty] | CONTROLLER 1 | Actual |  |  |  | CONTROLLER 1 | 41575 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC61 | MAY10DS010 | XC61 | SPEED CONTROLLER | - |  | Status | [9 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC01 | MAY10DS010 | XC01 | SPEED CONTROLLER | - |  | Feedback closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC02 | MAY10DS010 | XC02 | SPEED CONTROLLER | - |  | Feedback open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC20 | MAY10DS010 | XC20 | SPEED CONTROLLER | - | Control | Fault | 1 | bin | 0 | [6 empty] | CONTROLLER 1 | Fault |  |  |  | CONTROLLER 1 | 41577 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC81 | MAY10DS010 | XC81 | SPEED CONTROLLER | - |  | Ready for DCS set point link-on clc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC82 | MAY10DS010 | XC82 | SPEED CONTROLLER | - |  | Ready for DCS set point link-on olc | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC91 | MAY10DS010 | XC91 | SPEED CONTROLLER | - |  | Tracking command clc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC92 | MAY10DS010 | XC92 | SPEED CONTROLLER | - |  | Tracking command olc set point | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | ZB01 | MAY10DS010 | ZB01 | SPEED CONTROLLER | - |  | Protection on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | ZB02 | MAY10DS010 | ZB02 | SPEED CONTROLLER | - |  | Protection off | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS010 | XC98 | MAY10DS010 | XC98 | SPEED CONTROLLER | - |  | Operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 41577 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA91 | MAA10EC010 | XA91 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) | Control | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41643 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA61 | MAA10EC010 | XA61 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA01 | MAA10EC010 | XA01 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA02 | MAA10EC010 | XA02 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA03 | MAA10EC010 | XA03 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA04 | MAA10EC010 | XA04 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA20 | MAA10EC010 | XA20 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) | Control | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41645 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA08 | MAA10EC010 | XA08 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA09 | MAA10EC010 | XA09 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | ZA01 | MAA10EC010 | ZA01 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | ZA02 | MAA10EC010 | ZA02 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC010 | XA96 | MAA10EC010 | XA96 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41645 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA91 | MAA10EC050 | XA91 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41646 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA61 | MAA10EC050 | XA61 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA01 | MAA10EC050 | XA01 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA02 | MAA10EC050 | XA02 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA03 | MAA10EC050 | XA03 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA04 | MAA10EC050 | XA04 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA20 | MAA10EC050 | XA20 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41648 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA08 | MAA10EC050 | XA08 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA09 | MAA10EC050 | XA09 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | ZA01 | MAA10EC050 | ZA01 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | ZA02 | MAA10EC050 | ZA02 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC050 | XA96 | MAA10EC050 | XA96 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41648 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA91 | MAA10EC060 | XA91 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41649 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA61 | MAA10EC060 | XA61 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA01 | MAA10EC060 | XA01 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA02 | MAA10EC060 | XA02 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA03 | MAA10EC060 | XA03 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA04 | MAA10EC060 | XA04 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA20 | MAA10EC060 | XA20 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41651 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA08 | MAA10EC060 | XA08 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA09 | MAA10EC060 | XA09 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | ZA01 | MAA10EC060 | ZA01 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | ZA02 | MAA10EC060 | ZA02 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC060 | XA96 | MAA10EC060 | XA96 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41651 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA91 | MAA10EC070 | XA91 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41652 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA61 | MAA10EC070 | XA61 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA01 | MAA10EC070 | XA01 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA02 | MAA10EC070 | XA02 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA03 | MAA10EC070 | XA03 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA04 | MAA10EC070 | XA04 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA20 | MAA10EC070 | XA20 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41654 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA08 | MAA10EC070 | XA08 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA09 | MAA10EC070 | XA09 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | ZA01 | MAA10EC070 | ZA01 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | ZA02 | MAA10EC070 | ZA02 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC070 | XA96 | MAA10EC070 | XA96 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41654 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA91 | MAA10EC080 | XA91 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41655 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA61 | MAA10EC080 | XA61 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA01 | MAA10EC080 | XA01 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA02 | MAA10EC080 | XA02 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA03 | MAA10EC080 | XA03 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA04 | MAA10EC080 | XA04 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA20 | MAA10EC080 | XA20 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41657 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA08 | MAA10EC080 | XA08 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA09 | MAA10EC080 | XA09 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | ZA01 | MAA10EC080 | ZA01 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | ZA02 | MAA10EC080 | ZA02 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC080 | XA96 | MAA10EC080 | XA96 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41657 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA91 | MAL10EC010 | XA91 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41658 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA61 | MAL10EC010 | XA61 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA01 | MAL10EC010 | XA01 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA02 | MAL10EC010 | XA02 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA03 | MAL10EC010 | XA03 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA04 | MAL10EC010 | XA04 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA20 | MAL10EC010 | XA20 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41660 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA08 | MAL10EC010 | XA08 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA09 | MAL10EC010 | XA09 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | ZA01 | MAL10EC010 | ZA01 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | ZA02 | MAL10EC010 | ZA02 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL10EC010 | XA96 | MAL10EC010 | XA96 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41660 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA91 | MAV10EC010 | XA91 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41661 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA61 | MAV10EC010 | XA61 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA01 | MAV10EC010 | XA01 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA02 | MAV10EC010 | XA02 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA03 | MAV10EC010 | XA03 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA04 | MAV10EC010 | XA04 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA20 | MAV10EC010 | XA20 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41663 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA08 | MAV10EC010 | XA08 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA09 | MAV10EC010 | XA09 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | ZA01 | MAV10EC010 | ZA01 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | ZA02 | MAV10EC010 | ZA02 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10EC010 | XA96 | MAV10EC010 | XA96 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41663 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA91 | MAW10EC010 | XA91 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41664 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA61 | MAW10EC010 | XA61 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA01 | MAW10EC010 | XA01 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA02 | MAW10EC010 | XA02 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA03 | MAW10EC010 | XA03 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA04 | MAW10EC010 | XA04 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA20 | MAW10EC010 | XA20 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41666 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA08 | MAW10EC010 | XA08 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA09 | MAW10EC010 | XA09 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | ZA01 | MAW10EC010 | ZA01 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | ZA02 | MAW10EC010 | ZA02 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAW10EC010 | XA96 | MAW10EC010 | XA96 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41666 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA91 | MAX10EC010 | XA91 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41667 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA61 | MAX10EC010 | XA61 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA01 | MAX10EC010 | XA01 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA02 | MAX10EC010 | XA02 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA03 | MAX10EC010 | XA03 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA04 | MAX10EC010 | XA04 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA20 | MAX10EC010 | XA20 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41669 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA08 | MAX10EC010 | XA08 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA09 | MAX10EC010 | XA09 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | ZA01 | MAX10EC010 | ZA01 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | ZA02 | MAX10EC010 | ZA02 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10EC010 | XA96 | MAX10EC010 | XA96 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41669 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA91 | MAX40EC010 | XA91 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) | Monitoring | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41670 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA61 | MAX40EC010 | XA61 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA01 | MAX40EC010 | XA01 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA02 | MAX40EC010 | XA02 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA03 | MAX40EC010 | XA03 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA04 | MAX40EC010 | XA04 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA20 | MAX40EC010 | XA20 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) | Monitoring | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41672 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA08 | MAX40EC010 | XA08 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA09 | MAX40EC010 | XA09 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | ZA01 | MAX40EC010 | ZA01 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | ZA02 | MAX40EC010 | ZA02 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC010 | XA96 | MAX40EC010 | XA96 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41672 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA91 | MAX40EC020 | XA91 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41673 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA61 | MAX40EC020 | XA61 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA01 | MAX40EC020 | XA01 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA02 | MAX40EC020 | XA02 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA03 | MAX40EC020 | XA03 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA04 | MAX40EC020 | XA04 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA20 | MAX40EC020 | XA20 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41675 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA08 | MAX40EC020 | XA08 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA09 | MAX40EC020 | XA09 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | ZA01 | MAX40EC020 | ZA01 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | ZA02 | MAX40EC020 | ZA02 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC020 | XA96 | MAX40EC020 | XA96 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41675 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA91 | MAX40EC030 | XA91 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41676 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA61 | MAX40EC030 | XA61 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA01 | MAX40EC030 | XA01 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA02 | MAX40EC030 | XA02 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA03 | MAX40EC030 | XA03 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA04 | MAX40EC030 | XA04 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA20 | MAX40EC030 | XA20 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41678 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA08 | MAX40EC030 | XA08 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA09 | MAX40EC030 | XA09 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | ZA01 | MAX40EC030 | ZA01 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | ZA02 | MAX40EC030 | ZA02 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC030 | XA96 | MAX40EC030 | XA96 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41678 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA91 | MAX40EC050 | XA91 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41679 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA61 | MAX40EC050 | XA61 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA01 | MAX40EC050 | XA01 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA02 | MAX40EC050 | XA02 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA03 | MAX40EC050 | XA03 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA04 | MAX40EC050 | XA04 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA20 | MAX40EC050 | XA20 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41681 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA08 | MAX40EC050 | XA08 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA09 | MAX40EC050 | XA09 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | ZA01 | MAX40EC050 | ZA01 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | ZA02 | MAX40EC050 | ZA02 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC050 | XA96 | MAX40EC050 | XA96 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41681 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA91 | MAX40EC060 | XA91 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Step number | 0 | 100 | - | [6 empty] | STEP SEQUENCE | Step |  |  |  | STEP SEQUENCE | 41682 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA61 | MAX40EC060 | XA61 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Status | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA01 | MAX40EC060 | XA01 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Feedback on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA02 | MAX40EC060 | XA02 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Feedback off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA03 | MAX40EC060 | XA03 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Release op | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA04 | MAX40EC060 | XA04 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Release sd | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA20 | MAX40EC060 | XA20 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Fault | 1 | bin | 0 | [6 empty] | STEP SEQUENCE | Fault |  |  |  | STEP SEQUENCE | 41684 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA08 | MAX40EC060 | XA08 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Operation running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA09 | MAX40EC060 | XA09 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Shutdown running | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | ZA01 | MAX40EC060 | ZA01 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Protection operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | ZA02 | MAX40EC060 | ZA02 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Protection shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC060 | XA96 | MAX40EC060 | XA96 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 41684 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA450 | XQ52 | LBB10AA450 | XQ52 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT | Control | Actual set point | 0 | 100 | % | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41703 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA450 | XC61 | LBB10AA450 | XC61 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41705 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA450 | XC20 | LBB10AA450 | XC20 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41705 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA450 | XC82 | LBB10AA450 | XC82 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41705 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA450 | XQ52 | MAA10AA450 | XQ52 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT | Control | Actual set point | 0 | 100 | % | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41706 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA450 | XC61 | MAA10AA450 | XC61 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41708 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA450 | XC20 | MAA10AA450 | XC20 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41708 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA450 | XC82 | MAA10AA450 | XC82 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41708 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA460 | XQ52 | MAA10AA460 | XQ52 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT | Control | Actual set point | 0 | 100 | % | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41709 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA460 | XC61 | MAA10AA460 | XC61 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41711 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA460 | XC20 | MAA10AA460 | XC20 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41711 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA460 | XC82 | MAA10AA460 | XC82 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41711 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA470 | XQ52 | MAA10AA470 | XQ52 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT | Control | Actual set point | 0 | 100 | % | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41712 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA470 | XC61 | MAA10AA470 | XC61 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41714 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA470 | XC20 | MAA10AA470 | XC20 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41714 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA470 | XC82 | MAA10AA470 | XC82 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41714 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA480 | XQ52 | MAA10AA480 | XQ52 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT | Control | Actual set point | 0 | 100 | % | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41715 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA480 | XC61 | MAA10AA480 | XC61 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41717 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA480 | XC20 | MAA10AA480 | XC20 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41717 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA480 | XC82 | MAA10AA480 | XC82 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41717 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020A | XQ52 | MAY10DS020A | XQ52 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE | Control | Actual set point | 0 | 1 | bin | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41718 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020A | XC61 | MAY10DS020A | XC61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41720 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020A | XC20 | MAY10DS020A | XC20 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41720 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020A | XC82 | MAY10DS020A | XC82 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41720 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020B | XQ52 | MAY10DS020B | XQ52 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE | Control | Actual set point | 0 | 1 | bin | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41721 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020B | XC61 | MAY10DS020B | XC61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41723 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020B | XC20 | MAY10DS020B | XC20 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE | Control | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41723 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020B | XC82 | MAY10DS020B | XC82 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41723 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE060 | XQ52 | MKY10DE060 | XQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Actual set point | 0 | 22.8 | A | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41724 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE060 | XC61 | MKY10DE060 | XC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41726 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE060 | XC20 | MKY10DE060 | XC20 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41726 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE060 | XC82 | MKY10DE060 | XC82 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41726 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE063 | XQ52 | MKY10DE063 | XQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Actual set point | 11.04 | 16.56 | kV | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41727 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE063 | XC61 | MKY10DE063 | XC61 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41729 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE063 | XC20 | MKY10DE063 | XC20 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41729 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE063 | XC82 | MKY10DE063 | XC82 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41729 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE065 | XQ52 | MKY10DE065 | XQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Actual set point | 0,5 cap | 0,5 ind | - | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41730 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE065 | XC61 | MKY10DE065 | XC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41732 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE065 | XC20 | MKY10DE065 | XC20 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41732 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE065 | XC82 | MKY10DE065 | XC82 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41732 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE067 | XQ52 | MKY10DE067 | XQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Actual set point | -62.22 | 62.22 | MVAr | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41733 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE067 | XC61 | MKY10DE067 | XC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41735 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE067 | XC20 | MKY10DE067 | XC20 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41735 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE067 | XC82 | MKY10DE067 | XC82 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41735 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE069 | XQ52 | MKY10DE069 | XQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Actual set point | 0,5 cap | 0,5 ind | - | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41736 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE069 | XC61 | MKY10DE069 | XC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41738 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE069 | XC20 | MKY10DE069 | XC20 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41738 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE069 | XC82 | MKY10DE069 | XC82 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41738 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE071 | XQ52 | MKY10DE071 | XQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Actual set point | -62.22 | 62.22 | MVAr | [6 empty] | SETPOINT | Actual |  |  |  | SETPOINT | 41739 |  | read | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE071 | XC61 | MKY10DE071 | XC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Status | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 41741 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE071 | XC20 | MKY10DE071 | XC20 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Fault | 1 | bin | 0 | [6 empty] | SETPOINT | Fault |  |  |  | SETPOINT | 41741 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE071 | XC82 | MKY10DE071 | XC82 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Ready for DCS set point | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 41741 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB61 | MAK40AE110 | XB61 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41742 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB01 | MAK40AE110 | XB01 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB02 | MAK40AE110 | XB02 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB03 | MAK40AE110 | XB03 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB04 | MAK40AE110 | XB04 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB20 | MAK40AE110 | XB20 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41742 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XB96 | MAK40AE110 | XB96 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | ZB01 | MAK40AE110 | ZB01 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | ZB02 | MAK40AE110 | ZB02 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XA01 | MAK40AE110 | XA01 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAK40AE110 | XA02 | MAK40AE110 | XA02 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41742 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB61 | MAM65AN110 | XB61 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41743 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB01 | MAM65AN110 | XB01 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB02 | MAM65AN110 | XB02 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB03 | MAM65AN110 | XB03 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB04 | MAM65AN110 | XB04 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB20 | MAM65AN110 | XB20 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41743 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XB96 | MAM65AN110 | XB96 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | ZB01 | MAM65AN110 | ZB01 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | ZB02 | MAM65AN110 | ZB02 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XA01 | MAM65AN110 | XA01 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAM65AN110 | XA02 | MAM65AN110 | XA02 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41743 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB61 | MAV10AH110 | XB61 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41744 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB01 | MAV10AH110 | XB01 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB02 | MAV10AH110 | XB02 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB03 | MAV10AH110 | XB03 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB04 | MAV10AH110 | XB04 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB20 | MAV10AH110 | XB20 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41744 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XB96 | MAV10AH110 | XB96 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | ZB01 | MAV10AH110 | ZB01 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | ZB02 | MAV10AH110 | ZB02 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XA01 | MAV10AH110 | XA01 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10AH110 | XA02 | MAV10AH110 | XA02 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41744 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB61 | MAV15AN110 | XB61 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41745 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB01 | MAV15AN110 | XB01 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB02 | MAV15AN110 | XB02 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB03 | MAV15AN110 | XB03 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB04 | MAV15AN110 | XB04 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB20 | MAV15AN110 | XB20 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41745 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XB96 | MAV15AN110 | XB96 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | ZB01 | MAV15AN110 | ZB01 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | ZB02 | MAV15AN110 | ZB02 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XA01 | MAV15AN110 | XA01 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV15AN110 | XA02 | MAV15AN110 | XA02 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41745 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB61 | MAV21AP110 | XB61 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41746 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB01 | MAV21AP110 | XB01 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB02 | MAV21AP110 | XB02 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB03 | MAV21AP110 | XB03 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB04 | MAV21AP110 | XB04 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB20 | MAV21AP110 | XB20 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41746 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XB96 | MAV21AP110 | XB96 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | ZB01 | MAV21AP110 | ZB01 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | ZB02 | MAV21AP110 | ZB02 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XA01 | MAV21AP110 | XA01 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV21AP110 | XA02 | MAV21AP110 | XA02 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41746 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB61 | MAV25AP110 | XB61 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41747 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB01 | MAV25AP110 | XB01 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB02 | MAV25AP110 | XB02 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB03 | MAV25AP110 | XB03 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB04 | MAV25AP110 | XB04 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB20 | MAV25AP110 | XB20 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41747 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XB96 | MAV25AP110 | XB96 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | ZB01 | MAV25AP110 | ZB01 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | ZB02 | MAV25AP110 | ZB02 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XA01 | MAV25AP110 | XA01 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV25AP110 | XA02 | MAV25AP110 | XA02 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41747 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB61 | MAV70AP110 | XB61 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41748 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB01 | MAV70AP110 | XB01 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB02 | MAV70AP110 | XB02 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB03 | MAV70AP110 | XB03 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB04 | MAV70AP110 | XB04 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB20 | MAV70AP110 | XB20 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41748 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XB96 | MAV70AP110 | XB96 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | ZB01 | MAV70AP110 | ZB01 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | ZB02 | MAV70AP110 | ZB02 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XA01 | MAV70AP110 | XA01 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV70AP110 | XA02 | MAV70AP110 | XA02 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41748 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB61 | MAX10AH110 | XB61 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41749 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB01 | MAX10AH110 | XB01 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB02 | MAX10AH110 | XB02 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB03 | MAX10AH110 | XB03 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB04 | MAX10AH110 | XB04 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB20 | MAX10AH110 | XB20 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41749 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XB96 | MAX10AH110 | XB96 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | ZB01 | MAX10AH110 | ZB01 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | ZB02 | MAX10AH110 | ZB02 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XA01 | MAX10AH110 | XA01 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX10AH110 | XA02 | MAX10AH110 | XA02 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41749 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB61 | MAX51AP110 | XB61 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41750 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB01 | MAX51AP110 | XB01 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB02 | MAX51AP110 | XB02 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB03 | MAX51AP110 | XB03 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB04 | MAX51AP110 | XB04 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB20 | MAX51AP110 | XB20 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41750 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XB96 | MAX51AP110 | XB96 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | ZB01 | MAX51AP110 | ZB01 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | ZB02 | MAX51AP110 | ZB02 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XA01 | MAX51AP110 | XA01 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX51AP110 | XA02 | MAX51AP110 | XA02 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41750 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB61 | MKA10AH110 | XB61 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR |  |  |  |  | MOTOR | 41751 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB01 | MKA10AH110 | XB01 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB02 | MKA10AH110 | XB02 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB03 | MKA10AH110 | XB03 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB04 | MKA10AH110 | XB04 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB20 | MKA10AH110 | XB20 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR | Fault |  |  |  | MOTOR | 41751 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XB96 | MKA10AH110 | XB96 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | ZB01 | MKA10AH110 | ZB01 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | ZB02 | MKA10AH110 | ZB02 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XA01 | MKA10AH110 | XA01 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Feedback auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 10 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKA10AH110 | XA02 | MKA10AH110 | XA02 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Feedback manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 41751 | 11 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB61 | MAL20AP110 | XB61 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB01 | MAL20AP110 | XB01 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB02 | MAL20AP110 | XB02 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB03 | MAL20AP110 | XB03 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB04 | MAL20AP110 | XB04 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB20 | MAL20AP110 | XB20 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR with DCO | Fault |  |  |  | MOTOR with DCO | 41752 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | XB96 | MAL20AP110 | XB96 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | ZB01 | MAL20AP110 | ZB01 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20AP110 | ZB02 | MAL20AP110 | ZB02 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41752 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB61 | MAL30AP110 | XB61 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB01 | MAL30AP110 | XB01 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB02 | MAL30AP110 | XB02 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB03 | MAL30AP110 | XB03 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB04 | MAL30AP110 | XB04 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB20 | MAL30AP110 | XB20 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR with DCO | Fault |  |  |  | MOTOR with DCO | 41753 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | XB96 | MAL30AP110 | XB96 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | ZB01 | MAL30AP110 | ZB01 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL30AP110 | ZB02 | MAL30AP110 | ZB02 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41753 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB61 | MAX21AP110 | XB61 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB01 | MAX21AP110 | XB01 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB02 | MAX21AP110 | XB02 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB03 | MAX21AP110 | XB03 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB04 | MAX21AP110 | XB04 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB20 | MAX21AP110 | XB20 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR with DCO | Fault |  |  |  | MOTOR with DCO | 41754 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | XB96 | MAX21AP110 | XB96 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | ZB01 | MAX21AP110 | ZB01 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX21AP110 | ZB02 | MAX21AP110 | ZB02 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41754 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB61 | MAX22AP110 | XB61 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Status | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB01 | MAX22AP110 | XB01 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Feedback on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB02 | MAX22AP110 | XB02 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Feedback off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB03 | MAX22AP110 | XB03 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Release on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB04 | MAX22AP110 | XB04 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Release off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB20 | MAX22AP110 | XB20 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Fault | 1 | bin | 0 | [6 empty] | MOTOR with DCO | Fault |  |  |  | MOTOR with DCO | 41755 | 6 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | XB96 | MAX22AP110 | XB96 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | ZB01 | MAX22AP110 | ZB01 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Protection on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX22AP110 | ZB02 | MAX22AP110 | ZB02 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Protection off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 41755 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE244 | XA61 | MKY10EE244 | XA61 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Status | [9 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 41792 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE244 | XA11 | MKY10EE244 | XA11 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Device 1 selected | 1 | bin | 0 | [6 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 41792 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE244 | XA12 | MKY10EE244 | XA12 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Device 2 selected | 1 | bin | 0 | [6 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 41792 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE244 | XA03 | MKY10EE244 | XA03 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Release on | 1 | bin | 0 | [6 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 41792 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE244 | XA04 | MKY10EE244 | XA04 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Release off | 1 | bin | 0 | [6 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 41792 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA61 | MAL20EE010 | XA61 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Status | [9 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA01 | MAL20EE010 | XA01 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Feedback on | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA02 | MAL20EE010 | XA02 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Feedback off | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA03 | MAL20EE010 | XA03 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Release on | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA04 | MAL20EE010 | XA04 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Release off | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA11 | MAL20EE010 | XA11 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Device 1 selected | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA12 | MAL20EE010 | XA12 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Device 2 selected | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA20 | MAL20EE010 | XA20 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Fault | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER | Fault |  |  |  | DEVICE CHANGEOVER | 41802 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20EE010 | XA96 | MAL20EE010 | XA96 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Operator request | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41802 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA61 | MAX20EE010 | XA61 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Status | [9 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA01 | MAX20EE010 | XA01 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Feedback on | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA02 | MAX20EE010 | XA02 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Feedback off | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA03 | MAX20EE010 | XA03 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Release on | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA04 | MAX20EE010 | XA04 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Release off | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA11 | MAX20EE010 | XA11 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Device 1 selected | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA12 | MAX20EE010 | XA12 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Device 2 selected | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 5 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA20 | MAX20EE010 | XA20 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Fault | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER | Fault |  |  |  | DEVICE CHANGEOVER | 41803 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX20EE010 | XA96 | MAX20EE010 | XA96 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Operator request | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 41803 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB61 | LBB10AA240 | XB61 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41822 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB01 | LBB10AA240 | XB01 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB02 | LBB10AA240 | XB02 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB03 | LBB10AA240 | XB03 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB04 | LBB10AA240 | XB04 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB20 | LBB10AA240 | XB20 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41822 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | XB96 | LBB10AA240 | XB96 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | ZB01 | LBB10AA240 | ZB01 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10AA240 | ZB02 | LBB10AA240 | ZB02 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41822 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB61 | LBD20AA220 | XB61 | BLEED STEAM DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41823 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB01 | LBD20AA220 | XB01 | BLEED STEAM DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB02 | LBD20AA220 | XB02 | BLEED STEAM DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB03 | LBD20AA220 | XB03 | BLEED STEAM DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB04 | LBD20AA220 | XB04 | BLEED STEAM DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB20 | LBD20AA220 | XB20 | BLEED STEAM DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41823 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | XB96 | LBD20AA220 | XB96 | BLEED STEAM DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | ZB01 | LBD20AA220 | ZB01 | BLEED STEAM DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBD20AA220 | ZB02 | LBD20AA220 | ZB02 | BLEED STEAM DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41823 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB61 | LCE10AA210 | XB61 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41824 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB01 | LCE10AA210 | XB01 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB02 | LCE10AA210 | XB02 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB03 | LCE10AA210 | XB03 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB04 | LCE10AA210 | XB04 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB20 | LCE10AA210 | XB20 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41824 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | XB96 | LCE10AA210 | XB96 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | ZB01 | LCE10AA210 | ZB01 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE10AA210 | ZB02 | LCE10AA210 | ZB02 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41824 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB61 | LCE80AA210 | XB61 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41825 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB01 | LCE80AA210 | XB01 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB02 | LCE80AA210 | XB02 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB03 | LCE80AA210 | XB03 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB04 | LCE80AA210 | XB04 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB20 | LCE80AA210 | XB20 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41825 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | XB96 | LCE80AA210 | XB96 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | ZB01 | LCE80AA210 | ZB01 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE80AA210 | ZB02 | LCE80AA210 | ZB02 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41825 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB61 | MAA10AA210 | XB61 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41826 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB01 | MAA10AA210 | XB01 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB02 | MAA10AA210 | XB02 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB03 | MAA10AA210 | XB03 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB04 | MAA10AA210 | XB04 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB20 | MAA10AA210 | XB20 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41826 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | XB96 | MAA10AA210 | XB96 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | ZB01 | MAA10AA210 | ZB01 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA210 | ZB02 | MAA10AA210 | ZB02 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41826 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB61 | MAA10AA220 | XB61 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41827 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB01 | MAA10AA220 | XB01 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB02 | MAA10AA220 | XB02 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB03 | MAA10AA220 | XB03 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB04 | MAA10AA220 | XB04 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB20 | MAA10AA220 | XB20 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41827 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | XB96 | MAA10AA220 | XB96 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | ZB01 | MAA10AA220 | ZB01 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA220 | ZB02 | MAA10AA220 | ZB02 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41827 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB61 | MAA11AA210 | XB61 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41828 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB01 | MAA11AA210 | XB01 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB02 | MAA11AA210 | XB02 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB03 | MAA11AA210 | XB03 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB04 | MAA11AA210 | XB04 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB20 | MAA11AA210 | XB20 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41828 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | XB96 | MAA11AA210 | XB96 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | ZB01 | MAA11AA210 | ZB01 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA11AA210 | ZB02 | MAA11AA210 | ZB02 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41828 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB61 | MAA12AA210 | XB61 | DRAIN OF TURBINE CONTROL STAGE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41829 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB01 | MAA12AA210 | XB01 | DRAIN OF TURBINE CONTROL STAGE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB02 | MAA12AA210 | XB02 | DRAIN OF TURBINE CONTROL STAGE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB03 | MAA12AA210 | XB03 | DRAIN OF TURBINE CONTROL STAGE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB04 | MAA12AA210 | XB04 | DRAIN OF TURBINE CONTROL STAGE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB20 | MAA12AA210 | XB20 | DRAIN OF TURBINE CONTROL STAGE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41829 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | XB96 | MAA12AA210 | XB96 | DRAIN OF TURBINE CONTROL STAGE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | ZB01 | MAA12AA210 | ZB01 | DRAIN OF TURBINE CONTROL STAGE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA12AA210 | ZB02 | MAA12AA210 | ZB02 | DRAIN OF TURBINE CONTROL STAGE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41829 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB61 | MAA13AA210 | XB61 | TURBINE CASING DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41830 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB01 | MAA13AA210 | XB01 | TURBINE CASING DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB02 | MAA13AA210 | XB02 | TURBINE CASING DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB03 | MAA13AA210 | XB03 | TURBINE CASING DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB04 | MAA13AA210 | XB04 | TURBINE CASING DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB20 | MAA13AA210 | XB20 | TURBINE CASING DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41830 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | XB96 | MAA13AA210 | XB96 | TURBINE CASING DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | ZB01 | MAA13AA210 | ZB01 | TURBINE CASING DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA13AA210 | ZB02 | MAA13AA210 | ZB02 | TURBINE CASING DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41830 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB61 | MAA14AA210 | XB61 | ADMISSION STEAM DRAIN VALVE | - |  | Status | [9 empty] | VALVE |  |  |  |  | VALVE | 41831 |  | read | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB01 | MAA14AA210 | XB01 | ADMISSION STEAM DRAIN VALVE | - |  | Feedback on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 0 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB02 | MAA14AA210 | XB02 | ADMISSION STEAM DRAIN VALVE | - |  | Feedback off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 1 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB03 | MAA14AA210 | XB03 | ADMISSION STEAM DRAIN VALVE | - |  | Release on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 2 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB04 | MAA14AA210 | XB04 | ADMISSION STEAM DRAIN VALVE | - |  | Release off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 3 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB20 | MAA14AA210 | XB20 | ADMISSION STEAM DRAIN VALVE | - |  | Fault | 1 | bin | 0 | [6 empty] | VALVE | Fault |  |  |  | VALVE | 41831 | 4 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | XB96 | MAA14AA210 | XB96 | ADMISSION STEAM DRAIN VALVE | - |  | Operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 7 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | ZB01 | MAA14AA210 | ZB01 | ADMISSION STEAM DRAIN VALVE | - |  | Protection on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 8 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA14AA210 | ZB02 | MAA14AA210 | ZB02 | ADMISSION STEAM DRAIN VALVE | - |  | Protection off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 41831 | 9 | read | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EV010 | YQ80 | MAY10EV010 | YQ80 | DCS COUPLING WATCHDOG | - |  | Signal receive | 0 | 100 | [7 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45001 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-FI-6004 | XQ01 | LBA10CF010 | XQ01 | MAIN STEAM FLOW | - |  | Signal receive | 0 | 300000 | lbm/h | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45223 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-FI-6408 | XQ01 | LBD20CF010 | XQ01 | EXTRACTION PIPE FLOW | - |  | Signal receive | 0 | 120000 | lbm/h | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45225 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-FIT-6405 | XQ01 | LBB10CF010 | XQ01 | ADMISSION STEAM FLOW | - |  | Signal receive | 0 | 110000 | lbm/h | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45227 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-PI-6002 | XQ01 | LBA10CP010 | XQ01 | MAIN GATE VALVE INLET PRESSURE | - |  | Signal receive | 0 | 1450 | psi(g) | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45229 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-PIT-6425 | XQ01 | MAW10CP010 | XQ01 | SEAL STEAM CONTROL VALVE INLET PRESSURE | - |  | Signal receive | 0 | 1450 | psi(g) | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45231 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-TIT-6003 | XQ01 | LBA10CT010 | XQ01 | MAIN GATE VALVE INLET TEMPERATURE | - |  | Signal receive | 32 | 1112 | °F | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45233 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | 1560-TIT-6426 | XQ01 | MAW10CT010 | XQ01 | SEAL STEAM CONTROL VALVE INLET TEMPERATURE | - |  | Signal receive | 32 | 1112 | °F | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45235 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | 1560-ZI-6277 | XQ01 | LBD20CG010 | XQ01 | EXTRACTION STEAM NON RETURN VALVE POSITION | - |  | Signal receive | 0 | 100 | % | [6 empty] | ANALOG RECEIVE | Signal |  |  |  | ANALOG RECEIVE | 45237 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | YA61 | CBP10CE101 | YA61 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45313 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | YA11 | CBP10CE101 | YA11 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45313 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE101 | YA12 | CBP10CE101 | YA12 | SYNCHRONIZATION | GENERATOR CIRCUIT BREAKER REMOTE SELECT |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45313 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | YA61 | CBP10CE108 | YA61 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45314 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | YA11 | CBP10CE108 | YA11 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45314 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE108 | YA12 | CBP10CE108 | YA12 | SYNCHRONIZATION | NETWORK CIRCUIT BREAKER REMOTE SELECT |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45314 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | YA61 | CBP10CE110 | YA61 | SYNCHRONIZATION | REMOTE RESET LOR |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45315 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | YA11 | CBP10CE110 | YA11 | SYNCHRONIZATION | REMOTE RESET LOR |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45315 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | CBP10CE110 | YA12 | CBP10CE110 | YA12 | SYNCHRONIZATION | REMOTE RESET LOR |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45315 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | YA61 | CBP10CE111 | YA61 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45316 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | YA11 | CBP10CE111 | YA11 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45316 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | CBP10CE111 | YA12 | CBP10CE111 | YA12 | SYNCHRONIZATION | SYNCH RELEASED FROM TCS |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45316 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | YA61 | LBB10EE010 | YA61 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45317 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | YA11 | LBB10EE010 | YA11 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45317 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10EE010 | YA12 | LBB10EE010 | YA12 | SLC ADMISSION STEAM ESF OPEN | ACTIVE |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45317 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | YA61 | LBB10EE011 | YA61 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45318 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | YA11 | LBB10EE011 | YA11 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45318 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBB10EE011 | YA12 | LBB10EE011 | YA12 | SLC ADMISSION STEAM ESF CLOSE | ACTIVE |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45318 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | YA61 | LBE10EE010 | YA61 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45319 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | YA11 | LBE10EE010 | YA11 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45319 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBE10EE010 | YA12 | LBE10EE010 | YA12 | SLC CONFIRMATION EXHAUST STEAM GATE VALVE OPEN | ACTIVE |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45319 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | YA61 | MAA10EE010 | YA61 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45320 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | YA11 | MAA10EE010 | YA11 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45320 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EE010 | YA12 | MAA10EE010 | YA12 | SLC CORFIRMATION MAIN VALVE OPEN | ACTIVE |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45320 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | YA61 | MAV10EE011 | YA61 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45321 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | YA11 | MAV10EE011 | YA11 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45321 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EE011 | YA12 | MAV10EE011 | YA12 | FIRE PROTECTION OPERATOR VALIDATION | ACTIVE |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45321 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | YA61 | MAW10EE010 | YA61 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45322 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | YA11 | MAW10EE010 | YA11 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45322 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EE010 | YA12 | MAW10EE010 | YA12 | SLC STEAM TO GLAND SYSTEM PREHEATED | ACTIVE |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45322 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | YA61 | MAX40EE010 | YA61 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45323 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | YA11 | MAX40EE010 | YA11 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45323 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EE010 | YA12 | MAX40EE010 | YA12 | TEST HP CONTROL VALVES | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45323 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | YA61 | MAY10DS020 | YA61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45324 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | YA11 | MAY10DS020 | YA11 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45324 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020 | YA12 | MAY10DS020 | YA12 | FREQUENCY INFLUENCE ON LOAD CONTROLLER | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45324 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | YA61 | MAY10DS021 | YA61 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45325 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | YA11 | MAY10DS021 | YA11 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45325 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS021 | YA12 | MAY10DS021 | YA12 | FREQUENCYCORRECTOR | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45325 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | YA61 | MAY10EE010 | YA61 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45326 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | YA11 | MAY10EE010 | YA11 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45326 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE010 | YA12 | MAY10EE010 | YA12 | SPEED CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45326 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | YA61 | MAY10EE020 | YA61 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45327 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | YA11 | MAY10EE020 | YA11 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45327 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE020 | YA12 | MAY10EE020 | YA12 | LOAD CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45327 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | YA61 | MAY10EE030 | YA61 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45328 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | YA11 | MAY10EE030 | YA11 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45328 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE030 | YA12 | MAY10EE030 | YA12 | INLET PRESSURE CONTROLLER SELECTION | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45328 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | YA61 | MAY10EE220A | YA61 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45329 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | YA11 | MAY10EE220A | YA11 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45329 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE220A | YA12 | MAY10EE220A | YA12 | EXTRACTION PRESSURE CONTROLLER E1 | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45329 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | YA61 | MAY10EE910 | YA61 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45330 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | YA11 | MAY10EE910 | YA11 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45330 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EE910 | YA12 | MAY10EE910 | YA12 | TURBINE STARTUP, START | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45330 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | YA61 | MAY10EE920 | YA61 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45331 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | YA11 | MAY10EE920 | YA11 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45331 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10EE920 | YA12 | MAY10EE920 | YA12 | TURBINE STARTUP, STOP/CONTINUE | SUB LOOP CONTROL (SLC) |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45331 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | YA61 | MKY10EE230 | YA61 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45332 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | YA11 | MKY10EE230 | YA11 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45332 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE230 | YA12 | MKY10EE230 | YA12 | GENERATOR EXCITATION SYSTEM | EXCITATION ON / OFF |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45332 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | YA61 | MKY10EE231 | YA61 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45333 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | YA11 | MKY10EE231 | YA11 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45333 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE231 | YA12 | MKY10EE231 | YA12 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45333 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | YA61 | MKY10EE232 | YA61 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45334 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | YA11 | MKY10EE232 | YA11 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45334 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE232 | YA12 | MKY10EE232 | YA12 | GENERATOR EXCITATION SYSTEM | AUTOMATIC VOLTAGE CONTROL ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45334 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | YA61 | MKY10EE233 | YA61 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45335 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | YA11 | MKY10EE233 | YA11 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45335 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE233 | YA12 | MKY10EE233 | YA12 | GENERATOR EXCITATION SYSTEM | MANUAL ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45335 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | YA61 | MKY10EE234 | YA61 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45336 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | YA11 | MKY10EE234 | YA11 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45336 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE234 | YA12 | MKY10EE234 | YA12 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45336 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | YA61 | MKY10EE235 | YA61 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45337 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | YA11 | MKY10EE235 | YA11 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45337 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE235 | YA12 | MKY10EE235 | YA12 | GENERATOR EXCITATION SYSTEM | REACTIVE POWERCONTROL ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45337 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | YA61 | MKY10EE236 | YA61 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45338 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | YA11 | MKY10EE236 | YA11 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45338 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE236 | YA12 | MKY10EE236 | YA12 | GENERATOR EXCITATION SYSTEM | POWER FACTOR CONTROL NET COUPLING POINT ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45338 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | YA61 | MKY10EE237 | YA61 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45339 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | YA11 | MKY10EE237 | YA11 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45339 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE237 | YA12 | MKY10EE237 | YA12 | GENERATOR EXCITATION SYSTEM | REACTIVE POWER CONTROL NET COUPLING POINT ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45339 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | YA61 | MKY10EE245 | YA61 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45340 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | YA11 | MKY10EE245 | YA11 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45340 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE245 | YA12 | MKY10EE245 | YA12 | GENERATOR EXCITATION SYSTEM | POWER SYSTEM STABILIZER ON / OFF |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45340 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | YA61 | MKY10EE247 | YA61 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Commands | [9 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45341 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | YA11 | MKY10EE247 | YA11 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Command on | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45341 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10EE247 | YA12 | MKY10EE247 | YA12 | GENERATOR EXCITATION SYSTEM | Q=0 CONTROL NET COUPLING POINT ON |  | Command off | 1 | bin | 0 | [6 empty] | ON / OFF SELECTION |  |  |  |  | ON / OFF SELECTION | 45341 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | BCD10EU001 | XG01 | BCD10EU001 | XG01 | COOLING WATER SYSTEM TO TURBINE | READY FOR TURBINE START |  | Binary receive | 1 | bin | 0 | [6 empty] | SINGLE BINARY RECEIVE |  |  |  |  | SINGLE BINARY RECEIVE | 45343 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAG00EU001 | XG01 | MAG00EU001 | XG01 | CONDENSER SYSTEM | READY FOR TURBINE START |  | Binary receive | 1 | bin | 0 | [6 empty] | SINGLE BINARY RECEIVE |  |  |  |  | SINGLE BINARY RECEIVE | 45343 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10EZ100 | YA11 | MAY10EZ100 | YA11 | MANUAL TRIP ON OPERATOR STATION | - |  | Commands receive | 1 | bin | 0 | [6 empty] | SINGLE COMMAND RECEIVE |  |  |  |  | SINGLE COMMAND RECEIVE | 45343 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE238 | YA12 | MKY10DE238 | YA12 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE RAISE |  | Commands receive | 1 | bin | 0 | [6 empty] | SINGLE COMMAND RECEIVE |  |  |  |  | SINGLE COMMAND RECEIVE | 45343 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE238 | YA11 | MKY10DE238 | YA11 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE LOWER |  | Commands receive | 1 | bin | 0 | [6 empty] | SINGLE COMMAND RECEIVE |  |  |  |  | SINGLE COMMAND RECEIVE | 45343 | 4 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | YQ51 | MAY10DE020 | YQ51 | LOAD CONTROLLER | - |  | DCS set point signal clc | 0 | 35.89 | MW | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46543 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | YQ52 | MAY10DE020 | YQ52 | LOAD CONTROLLER | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46545 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | YC01 | MAY10DE020 | YC01 | LOAD CONTROLLER | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46547 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | YC02 | MAY10DE020 | YC02 | LOAD CONTROLLER | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46547 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | YC10 | MAY10DE020 | YC10 | LOAD CONTROLLER | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46547 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DE020 | YC98 | MAY10DE020 | YC98 | LOAD CONTROLLER | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46547 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE120 | YQ51 | MAY10DE120 | YQ51 | LOAD LIMIT CONTROLLER | - |  | DCS set point signal clc | 0 | 35.89 | MW | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46548 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE120 | YQ52 | MAY10DE120 | YQ52 | LOAD LIMIT CONTROLLER | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46550 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE120 | YC01 | MAY10DE120 | YC01 | LOAD LIMIT CONTROLLER | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46552 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE120 | YC02 | MAY10DE120 | YC02 | LOAD LIMIT CONTROLLER | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46552 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE120 | YC10 | MAY10DE120 | YC10 | LOAD LIMIT CONTROLLER | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46552 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DE120 | YC98 | MAY10DE120 | YC98 | LOAD LIMIT CONTROLLER | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46552 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP030 | YQ51 | MAY10DP030 | YQ51 | INLET PRESSURE CONTROLLER | - |  | DCS set point signal clc | 825.8 | 914.5 | psi(g) | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46553 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP030 | YQ52 | MAY10DP030 | YQ52 | INLET PRESSURE CONTROLLER | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46555 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP030 | YC01 | MAY10DP030 | YC01 | INLET PRESSURE CONTROLLER | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46557 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP030 | YC02 | MAY10DP030 | YC02 | INLET PRESSURE CONTROLLER | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46557 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP030 | YC10 | MAY10DP030 | YC10 | INLET PRESSURE CONTROLLER | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46557 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP030 | YC98 | MAY10DP030 | YC98 | INLET PRESSURE CONTROLLER | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46557 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP050 | YQ51 | MAY10DP050 | YQ51 | ADMISSION PRESSURE CONTROLLER | - |  | DCS set point signal clc | 0 | 1 | bin | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46558 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP050 | YQ52 | MAY10DP050 | YQ52 | ADMISSION PRESSURE CONTROLLER | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46560 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP050 | YC01 | MAY10DP050 | YC01 | ADMISSION PRESSURE CONTROLLER | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46562 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP050 | YC02 | MAY10DP050 | YC02 | ADMISSION PRESSURE CONTROLLER | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46562 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP050 | YC10 | MAY10DP050 | YC10 | ADMISSION PRESSURE CONTROLLER | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46562 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP050 | YC98 | MAY10DP050 | YC98 | ADMISSION PRESSURE CONTROLLER | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46562 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP130 | YQ51 | MAY10DP130 | YQ51 | INLET PRESSURE LIMIT CONTROLLER | - |  | DCS set point signal clc | 825.8 | 914.5 | psi(g) | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46563 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP130 | YQ52 | MAY10DP130 | YQ52 | INLET PRESSURE LIMIT CONTROLLER | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46565 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP130 | YC01 | MAY10DP130 | YC01 | INLET PRESSURE LIMIT CONTROLLER | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46567 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP130 | YC02 | MAY10DP130 | YC02 | INLET PRESSURE LIMIT CONTROLLER | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46567 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP130 | YC10 | MAY10DP130 | YC10 | INLET PRESSURE LIMIT CONTROLLER | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46567 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DP130 | YC98 | MAY10DP130 | YC98 | INLET PRESSURE LIMIT CONTROLLER | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46567 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP210 | YQ51 | MAY10DP210 | YQ51 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | DCS set point signal clc | 61.79 | 77.74 | psi(g) | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46568 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP210 | YQ52 | MAY10DP210 | YQ52 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46570 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP210 | YC01 | MAY10DP210 | YC01 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46572 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP210 | YC02 | MAY10DP210 | YC02 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46572 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP210 | YC10 | MAY10DP210 | YC10 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46572 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DP210 | YC98 | MAY10DP210 | YC98 | EXTRACTION PRESSURE CONTROLLER E1 | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46572 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS010 | YQ51 | MAY10DS010 | YQ51 | SPEED CONTROLLER | - |  | DCS set point signal clc | 0 | 7737 | rpm | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46573 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS010 | YQ52 | MAY10DS010 | YQ52 | SPEED CONTROLLER | - |  | DCS set point signal olc | 0 | 100 | % | [6 empty] | CONTROLLER 1 | DCS |  |  |  | CONTROLLER 1 | 46575 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS010 | YC01 | MAY10DS010 | YC01 | SPEED CONTROLLER | - |  | Command closed loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46577 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS010 | YC02 | MAY10DS010 | YC02 | SPEED CONTROLLER | - |  | Command open loop | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46577 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS010 | YC10 | MAY10DS010 | YC10 | SPEED CONTROLLER | - |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46577 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS010 | YC98 | MAY10DS010 | YC98 | SPEED CONTROLLER | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | CONTROLLER 1 |  |  |  |  | CONTROLLER 1 | 46577 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC010 | YA61 | MAA10EC010 | YA61 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46645 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC010 | YA11 | MAA10EC010 | YA11 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46645 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC010 | YA12 | MAA10EC010 | YA12 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46645 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC010 | YA18 | MAA10EC010 | YA18 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46645 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC010 | YA19 | MAA10EC010 | YA19 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46645 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC010 | YA96 | MAA10EC010 | YA96 | GROUP CONTROL TURBINE | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46645 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC050 | YA61 | MAA10EC050 | YA61 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46648 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC050 | YA11 | MAA10EC050 | YA11 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46648 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC050 | YA12 | MAA10EC050 | YA12 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46648 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC050 | YA18 | MAA10EC050 | YA18 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46648 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC050 | YA19 | MAA10EC050 | YA19 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46648 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC050 | YA96 | MAA10EC050 | YA96 | HP ACTUATING VALVE 1 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46648 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC060 | YA61 | MAA10EC060 | YA61 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46651 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC060 | YA11 | MAA10EC060 | YA11 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46651 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC060 | YA12 | MAA10EC060 | YA12 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46651 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC060 | YA18 | MAA10EC060 | YA18 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46651 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC060 | YA19 | MAA10EC060 | YA19 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46651 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC060 | YA96 | MAA10EC060 | YA96 | HP ACTUATING VALVE 2 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46651 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC070 | YA61 | MAA10EC070 | YA61 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46654 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC070 | YA11 | MAA10EC070 | YA11 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46654 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC070 | YA12 | MAA10EC070 | YA12 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46654 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC070 | YA18 | MAA10EC070 | YA18 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46654 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC070 | YA19 | MAA10EC070 | YA19 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46654 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10EC070 | YA96 | MAA10EC070 | YA96 | HP ACTUATING VALVE 3 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46654 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC080 | YA61 | MAA10EC080 | YA61 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46657 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC080 | YA11 | MAA10EC080 | YA11 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46657 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC080 | YA12 | MAA10EC080 | YA12 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46657 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC080 | YA18 | MAA10EC080 | YA18 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46657 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC080 | YA19 | MAA10EC080 | YA19 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46657 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10EC080 | YA96 | MAA10EC080 | YA96 | HP ACTUATING VALVE 4 MOVEMENT TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46657 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL10EC010 | YA61 | MAL10EC010 | YA61 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46660 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAL10EC010 | YA11 | MAL10EC010 | YA11 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46660 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL10EC010 | YA12 | MAL10EC010 | YA12 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46660 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL10EC010 | YA18 | MAL10EC010 | YA18 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46660 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL10EC010 | YA19 | MAL10EC010 | YA19 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46660 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL10EC010 | YA96 | MAL10EC010 | YA96 | GROUP CONTROL DRAIN SYSTEM | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46660 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EC010 | YA61 | MAV10EC010 | YA61 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46663 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EC010 | YA11 | MAV10EC010 | YA11 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46663 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EC010 | YA12 | MAV10EC010 | YA12 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46663 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EC010 | YA18 | MAV10EC010 | YA18 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46663 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EC010 | YA19 | MAV10EC010 | YA19 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46663 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV10EC010 | YA96 | MAV10EC010 | YA96 | GROUP CONTROL OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46663 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EC010 | YA61 | MAW10EC010 | YA61 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46666 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EC010 | YA11 | MAW10EC010 | YA11 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46666 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EC010 | YA12 | MAW10EC010 | YA12 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46666 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EC010 | YA18 | MAW10EC010 | YA18 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46666 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EC010 | YA19 | MAW10EC010 | YA19 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46666 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAW10EC010 | YA96 | MAW10EC010 | YA96 | GROUP CONTROL GLAND STEAM | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46666 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10EC010 | YA61 | MAX10EC010 | YA61 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46669 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10EC010 | YA11 | MAX10EC010 | YA11 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46669 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10EC010 | YA12 | MAX10EC010 | YA12 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46669 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10EC010 | YA18 | MAX10EC010 | YA18 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46669 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10EC010 | YA19 | MAX10EC010 | YA19 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46669 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10EC010 | YA96 | MAX10EC010 | YA96 | GROUP CONTROL HP OIL SYSTEM | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46669 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC010 | YA61 | MAX40EC010 | YA61 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46672 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC010 | YA11 | MAX40EC010 | YA11 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46672 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC010 | YA12 | MAX40EC010 | YA12 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46672 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC010 | YA18 | MAX40EC010 | YA18 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46672 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC010 | YA19 | MAX40EC010 | YA19 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46672 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC010 | YA96 | MAX40EC010 | YA96 | SGC TURBINE PROTECTION SYSTEM ACTIVATION | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46672 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC020 | YA61 | MAX40EC020 | YA61 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46675 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC020 | YA11 | MAX40EC020 | YA11 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46675 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC020 | YA12 | MAX40EC020 | YA12 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46675 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC020 | YA18 | MAX40EC020 | YA18 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46675 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC020 | YA19 | MAX40EC020 | YA19 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46675 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC020 | YA96 | MAX40EC020 | YA96 | SGC TRIP ACTIVATION CHANNEL TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46675 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC030 | YA61 | MAX40EC030 | YA61 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46678 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC030 | YA11 | MAX40EC030 | YA11 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46678 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC030 | YA12 | MAX40EC030 | YA12 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46678 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC030 | YA18 | MAX40EC030 | YA18 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46678 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC030 | YA19 | MAX40EC030 | YA19 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46678 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC030 | YA96 | MAX40EC030 | YA96 | SGC OVERSPEED PROTECTION CHANNEL TEST (HP) | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46678 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC050 | YA61 | MAX40EC050 | YA61 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46681 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC050 | YA11 | MAX40EC050 | YA11 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46681 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC050 | YA12 | MAX40EC050 | YA12 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46681 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC050 | YA18 | MAX40EC050 | YA18 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46681 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC050 | YA19 | MAX40EC050 | YA19 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46681 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX40EC050 | YA96 | MAX40EC050 | YA96 | SGC MAIN STOP VALVE 1 PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46681 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC060 | YA61 | MAX40EC060 | YA61 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Commands | [9 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46684 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC060 | YA11 | MAX40EC060 | YA11 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command on | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46684 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC060 | YA12 | MAX40EC060 | YA12 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command off | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46684 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC060 | YA18 | MAX40EC060 | YA18 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command operation | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46684 | 2 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC060 | YA19 | MAX40EC060 | YA19 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Command shutdown | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46684 | 3 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX40EC060 | YA96 | MAX40EC060 | YA96 | SGC ADMISSION STEAM ESF PARTIAL STROKE TEST | SUP GROUP CONTROL (SGC) |  | Reset operator request | 1 | bin | 0 | [6 empty] | STEP SEQUENCE |  |  |  |  | STEP SEQUENCE | 46684 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA450 | YQ52 | LBB10AA450 | YQ52 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46703 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA450 | YQ52 | LBB10AA450 | YQ52 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46703 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA450 | YC61 | LBB10AA450 | YC61 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46705 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA450 | YC61 | LBB10AA450 | YC61 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46705 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA450 | YC10 | LBB10AA450 | YC10 | HP ADMISION STEAM CONTROL VALVE | TEST SETPOINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46705 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | YQ52 | MAA10AA450 | YQ52 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46706 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | YQ52 | MAA10AA450 | YQ52 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46706 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | YC61 | MAA10AA450 | YC61 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46708 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | YC61 | MAA10AA450 | YC61 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46708 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA450 | YC10 | MAA10AA450 | YC10 | HP STEAM CONTROL VALVE 1 | TEST SETPOINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46708 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | YQ52 | MAA10AA460 | YQ52 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46709 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | YQ52 | MAA10AA460 | YQ52 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46709 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | YC61 | MAA10AA460 | YC61 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46711 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | YC61 | MAA10AA460 | YC61 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46711 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA460 | YC10 | MAA10AA460 | YC10 | HP STEAM CONTROL VALVE 2 | TEST SETPOINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46711 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | YQ52 | MAA10AA470 | YQ52 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46712 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | YQ52 | MAA10AA470 | YQ52 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46712 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | YC61 | MAA10AA470 | YC61 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46714 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | YC61 | MAA10AA470 | YC61 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46714 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA470 | YC10 | MAA10AA470 | YC10 | HP STEAM CONTROL VALVE 3 | TEST SETPOINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46714 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | YQ52 | MAA10AA480 | YQ52 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46715 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | YQ52 | MAA10AA480 | YQ52 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | DCS set point | 0 | 100 | % | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46715 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | YC61 | MAA10AA480 | YC61 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46717 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | YC61 | MAA10AA480 | YC61 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46717 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA480 | YC10 | MAA10AA480 | YC10 | HP STEAM CONTROL VALVE 4 | TEST SETPOINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46717 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020A | YQ52 | MAY10DS020A | YQ52 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | DCS set point | 0 | 1 | bin | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46718 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020A | YQ52 | MAY10DS020A | YQ52 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | DCS set point | 0 | 1 | bin | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46718 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020A | YC61 | MAY10DS020A | YC61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46720 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020A | YC61 | MAY10DS020A | YC61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46720 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAY10DS020A | YC10 | MAY10DS020A | YC10 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DEADBAND) | INTERFERENCE VALUE |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46720 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020B | YQ52 | MAY10DS020B | YQ52 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | DCS set point | 0 | 1 | bin | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46721 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020B | YQ52 | MAY10DS020B | YQ52 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | DCS set point | 0 | 1 | bin | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46721 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020B | YC61 | MAY10DS020B | YC61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46723 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020B | YC61 | MAY10DS020B | YC61 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46723 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAY10DS020B | YC10 | MAY10DS020B | YC10 | FREQUENCY INFLUENCE ON LOAD CONTROLLER (DROOP) | INTERFERENCE VALUE |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46723 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE060 | YQ52 | MKY10DE060 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | DCS set point | 0 | 22.8 | A | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46724 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE060 | YQ52 | MKY10DE060 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | DCS set point | 0 | 22.8 | A | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46724 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE060 | YC61 | MKY10DE060 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46726 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE060 | YC61 | MKY10DE060 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46726 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE060 | YC10 | MKY10DE060 | YC10 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE EXCITATION CURRENT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46726 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE063 | YQ52 | MKY10DE063 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | DCS set point | 11.04 | 16.56 | kV | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46727 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE063 | YQ52 | MKY10DE063 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | DCS set point | 11.04 | 16.56 | kV | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46727 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE063 | YC61 | MKY10DE063 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46729 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE063 | YC61 | MKY10DE063 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46729 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE063 | YC10 | MKY10DE063 | YC10 | GENERATOR EXCITATION SYSTEM | REFERENCE GENERATOR VOLTAGE |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46729 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE065 | YQ52 | MKY10DE065 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | DCS set point | 0,5 cap | 0,5 ind | - | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46730 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE065 | YQ52 | MKY10DE065 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | DCS set point | 0,5 cap | 0,5 ind | - | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46730 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE065 | YC61 | MKY10DE065 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46732 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE065 | YC61 | MKY10DE065 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46732 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE065 | YC10 | MKY10DE065 | YC10 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR GENERATOR |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46732 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE067 | YQ52 | MKY10DE067 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | DCS set point | -62.22 | 62.22 | MVAr | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46733 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE067 | YQ52 | MKY10DE067 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | DCS set point | -62.22 | 62.22 | MVAr | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46733 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE067 | YC61 | MKY10DE067 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46735 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE067 | YC61 | MKY10DE067 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46735 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE067 | YC10 | MKY10DE067 | YC10 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER GENERATOR |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46735 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE069 | YQ52 | MKY10DE069 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | DCS set point | 0,5 cap | 0,5 ind | - | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46736 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE069 | YQ52 | MKY10DE069 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | DCS set point | 0,5 cap | 0,5 ind | - | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46736 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE069 | YC61 | MKY10DE069 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46738 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE069 | YC61 | MKY10DE069 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46738 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10DE069 | YC10 | MKY10DE069 | YC10 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE POWER FACTOR NET COUPLING POINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46738 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE071 | YQ52 | MKY10DE071 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | DCS set point | -62.22 | 62.22 | MVAr | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46739 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE071 | YQ52 | MKY10DE071 | YQ52 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | DCS set point | -62.22 | 62.22 | MVAr | [6 empty] | SETPOINT | DCS |  |  |  | SETPOINT | 46739 |  | write | REAL | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE071 | YC61 | MKY10DE071 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46741 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE071 | YC61 | MKY10DE071 | YC61 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Commands | [9 empty] | SETPOINT |  |  |  |  | SETPOINT | 46741 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKY10DE071 | YC10 | MKY10DE071 | YC10 | GENERATOR EXCITATION SYSTEM | REFERENCE VALUE REACTIVE POWER NET COUPLING POINT |  | Command DCS setpoint link-on | 1 | bin | 0 | [6 empty] | SETPOINT |  |  |  |  | SETPOINT | 46741 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAK40AE110 | YB61 | MAK40AE110 | YB61 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46742 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAK40AE110 | YB11 | MAK40AE110 | YB11 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46742 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAK40AE110 | YB12 | MAK40AE110 | YB12 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46742 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAK40AE110 | YB96 | MAK40AE110 | YB96 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46742 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAK40AE110 | YA01 | MAK40AE110 | YA01 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46742 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAK40AE110 | YA02 | MAK40AE110 | YA02 | TURNING GEAR | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46742 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAM65AN110 | YB61 | MAM65AN110 | YB61 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46743 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAM65AN110 | YB11 | MAM65AN110 | YB11 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46743 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAM65AN110 | YB12 | MAM65AN110 | YB12 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46743 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAM65AN110 | YB96 | MAM65AN110 | YB96 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46743 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAM65AN110 | YA01 | MAM65AN110 | YA01 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46743 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAM65AN110 | YA02 | MAM65AN110 | YA02 | WASTE STEAM CONDENSER SUCTION FAN | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46743 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10AH110 | YB61 | MAV10AH110 | YB61 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46744 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10AH110 | YB11 | MAV10AH110 | YB11 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46744 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10AH110 | YB12 | MAV10AH110 | YB12 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46744 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10AH110 | YB96 | MAV10AH110 | YB96 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46744 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10AH110 | YA01 | MAV10AH110 | YA01 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46744 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV10AH110 | YA02 | MAV10AH110 | YA02 | LUBE OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46744 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV15AN110 | YB61 | MAV15AN110 | YB61 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46745 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV15AN110 | YB11 | MAV15AN110 | YB11 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46745 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV15AN110 | YB12 | MAV15AN110 | YB12 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46745 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV15AN110 | YB96 | MAV15AN110 | YB96 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46745 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV15AN110 | YA01 | MAV15AN110 | YA01 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46745 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV15AN110 | YA02 | MAV15AN110 | YA02 | OIL MIST SEPARATOR FAN | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46745 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV21AP110 | YB61 | MAV21AP110 | YB61 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46746 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAV21AP110 | YB11 | MAV21AP110 | YB11 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46746 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV21AP110 | YB12 | MAV21AP110 | YB12 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46746 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV21AP110 | YB96 | MAV21AP110 | YB96 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46746 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV21AP110 | YA01 | MAV21AP110 | YA01 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46746 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV21AP110 | YA02 | MAV21AP110 | YA02 | AUXILIARY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46746 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | YB61 | MAV25AP110 | YB61 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46747 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | YB11 | MAV25AP110 | YB11 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46747 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | YB12 | MAV25AP110 | YB12 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46747 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | YB96 | MAV25AP110 | YB96 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46747 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | YA01 | MAV25AP110 | YA01 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46747 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAV25AP110 | YA02 | MAV25AP110 | YA02 | EMERGENCY OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46747 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV70AP110 | YB61 | MAV70AP110 | YB61 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46748 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAV70AP110 | YB11 | MAV70AP110 | YB11 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46748 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV70AP110 | YB12 | MAV70AP110 | YB12 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46748 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV70AP110 | YB96 | MAV70AP110 | YB96 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46748 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV70AP110 | YA01 | MAV70AP110 | YA01 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46748 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAV70AP110 | YA02 | MAV70AP110 | YA02 | JACKING OIL PUMP | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46748 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10AH110 | YB61 | MAX10AH110 | YB61 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46749 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10AH110 | YB11 | MAX10AH110 | YB11 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46749 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10AH110 | YB12 | MAX10AH110 | YB12 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46749 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10AH110 | YB96 | MAX10AH110 | YB96 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46749 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10AH110 | YA01 | MAX10AH110 | YA01 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46749 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX10AH110 | YA02 | MAX10AH110 | YA02 | CONTROL OIL TANK HEATING | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46749 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX51AP110 | YB61 | MAX51AP110 | YB61 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46750 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX51AP110 | YB11 | MAX51AP110 | YB11 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46750 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX51AP110 | YB12 | MAX51AP110 | YB12 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46750 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX51AP110 | YB96 | MAX51AP110 | YB96 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46750 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX51AP110 | YA01 | MAX51AP110 | YA01 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46750 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX51AP110 | YA02 | MAX51AP110 | YA02 | CONTROL OIL COOLER PUMP | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46750 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKA10AH110 | YB61 | MKA10AH110 | YB61 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR |  |  |  |  | MOTOR | 46751 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MKA10AH110 | YB11 | MKA10AH110 | YB11 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46751 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKA10AH110 | YB12 | MKA10AH110 | YB12 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46751 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKA10AH110 | YB96 | MKA10AH110 | YB96 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46751 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKA10AH110 | YA01 | MKA10AH110 | YA01 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Command auto | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46751 | 10 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MKA10AH110 | YA02 | MKA10AH110 | YA02 | GENERATOR ANTI-CONDENSATION HEATER | DRIVE CONTROL (MOTOR) |  | Command manual | 1 | bin | 0 | [6 empty] | MOTOR |  |  |  |  | MOTOR | 46751 | 11 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20AP110 | YB61 | MAL20AP110 | YB61 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46752 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20AP110 | YB11 | MAL20AP110 | YB11 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46752 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20AP110 | YB12 | MAL20AP110 | YB12 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46752 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAL20AP110 | YB96 | MAL20AP110 | YB96 | DRAIN TANK PUMP 1 | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46752 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL30AP110 | YB61 | MAL30AP110 | YB61 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46753 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAL30AP110 | YB11 | MAL30AP110 | YB11 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46753 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL30AP110 | YB12 | MAL30AP110 | YB12 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46753 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL30AP110 | YB96 | MAL30AP110 | YB96 | DRAIN TANK PUMP 2 | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46753 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX21AP110 | YB61 | MAX21AP110 | YB61 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46754 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX21AP110 | YB11 | MAX21AP110 | YB11 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46754 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX21AP110 | YB12 | MAX21AP110 | YB12 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46754 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX21AP110 | YB96 | MAX21AP110 | YB96 | CONTROL OIL PUMP 1 | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46754 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX22AP110 | YB61 | MAX22AP110 | YB61 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Commands | [9 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46755 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAX22AP110 | YB11 | MAX22AP110 | YB11 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Command on | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46755 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX22AP110 | YB12 | MAX22AP110 | YB12 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Command off | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46755 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAX22AP110 | YB96 | MAX22AP110 | YB96 | CONTROL OIL PUMP 2 | DRIVE CONTROL (MOTOR) |  | Reset operator request | 1 | bin | 0 | [6 empty] | MOTOR with DCO |  |  |  |  | MOTOR with DCO | 46755 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE244 | YA61 | MKY10EE244 | YA61 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Commands | [9 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 46792 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE244 | YA21 | MKY10EE244 | YA21 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Command device 1 select | 1 | bin | 0 | [6 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 46792 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MKY10EE244 | YA22 | MKY10EE244 | YA22 | GENERATOR EXCITATION SYSTEM | CHANNEL SWITCH OVER |  | Command device 2 select | 1 | bin | 0 | [6 empty] | PRE-SELECTION |  |  |  |  | PRE-SELECTION | 46792 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20EE010 | YA61 | MAL20EE010 | YA61 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Commands | [9 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46802 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20EE010 | YA11 | MAL20EE010 | YA11 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Command on | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46802 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20EE010 | YA12 | MAL20EE010 | YA12 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Command off | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46802 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20EE010 | YA21 | MAL20EE010 | YA21 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Command device 1 select | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46802 | 4 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20EE010 | YA22 | MAL20EE010 | YA22 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Command device 2 select | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46802 | 5 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAL20EE010 | YA96 | MAL20EE010 | YA96 | DCO DRAIN TANK PUMPS | device change over automatic (DCO) |  | Reset operator request | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46802 | 8 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | YA61 | MAX20EE010 | YA61 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Commands | [9 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46803 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | YA11 | MAX20EE010 | YA11 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Command on | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46803 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | YA12 | MAX20EE010 | YA12 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Command off | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46803 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | YA21 | MAX20EE010 | YA21 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Command device 1 select | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46803 | 4 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | YA22 | MAX20EE010 | YA22 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Command device 2 select | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46803 | 5 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAX20EE010 | YA96 | MAX20EE010 | YA96 | DCO CONTROL OIL PUMPS | DEVICE CHANGE OVER AUTOMATIC (DCO) |  | Reset operator request | 1 | bin | 0 | [6 empty] | DEVICE CHANGEOVER |  |  |  |  | DEVICE CHANGEOVER | 46803 | 8 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA240 | YB61 | LBB10AA240 | YB61 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46822 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA240 | YB11 | LBB10AA240 | YB11 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46822 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA240 | YB12 | LBB10AA240 | YB12 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46822 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LBB10AA240 | YB96 | LBB10AA240 | YB96 | EMERGENCY STOP FLAP DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46822 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD20AA220 | YB61 | LBD20AA220 | YB61 | BLEED STEAM DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46823 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LBD20AA220 | YB11 | LBD20AA220 | YB11 | BLEED STEAM DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46823 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD20AA220 | YB12 | LBD20AA220 | YB12 | BLEED STEAM DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46823 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LBD20AA220 | YB96 | LBD20AA220 | YB96 | BLEED STEAM DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46823 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE10AA210 | YB61 | LCE10AA210 | YB61 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46824 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | LCE10AA210 | YB11 | LCE10AA210 | YB11 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46824 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE10AA210 | YB12 | LCE10AA210 | YB12 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46824 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | LCE10AA210 | YB96 | LCE10AA210 | YB96 | EXHAUST STEAM CONDENSATE INJECTION SOV | SOLENOID VALVE CTRL |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46824 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE80AA210 | YB61 | LCE80AA210 | YB61 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46825 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | LCE80AA210 | YB11 | LCE80AA210 | YB11 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46825 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE80AA210 | YB12 | LCE80AA210 | YB12 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46825 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | LCE80AA210 | YB96 | LCE80AA210 | YB96 | FLASH PIPE CONDENSATE INJECTION VALVE | SOLENOID VALVE CTRL (SOV) |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46825 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA210 | YB61 | MAA10AA210 | YB61 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46826 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA210 | YB11 | MAA10AA210 | YB11 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46826 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA210 | YB12 | MAA10AA210 | YB12 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46826 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA10AA210 | YB96 | MAA10AA210 | YB96 | EMERGENCY STOP VALVE DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46826 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA220 | YB61 | MAA10AA220 | YB61 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46827 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA220 | YB11 | MAA10AA220 | YB11 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46827 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA220 | YB12 | MAA10AA220 | YB12 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46827 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA10AA220 | YB96 | MAA10AA220 | YB96 | CONTROL VALVE INLET MAIN STEAM DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46827 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA11AA210 | YB61 | MAA11AA210 | YB61 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46828 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA11AA210 | YB11 | MAA11AA210 | YB11 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46828 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA11AA210 | YB12 | MAA11AA210 | YB12 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46828 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA11AA210 | YB96 | MAA11AA210 | YB96 | BALANCE PISTON AK1 DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46828 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA12AA210 | YB61 | MAA12AA210 | YB61 | DRAIN OF TURBINE CONTROL STAGE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46829 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA12AA210 | YB11 | MAA12AA210 | YB11 | DRAIN OF TURBINE CONTROL STAGE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46829 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA12AA210 | YB12 | MAA12AA210 | YB12 | DRAIN OF TURBINE CONTROL STAGE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46829 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA12AA210 | YB96 | MAA12AA210 | YB96 | DRAIN OF TURBINE CONTROL STAGE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46829 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA13AA210 | YB61 | MAA13AA210 | YB61 | TURBINE CASING DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46830 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | -1 | MAA13AA210 | YB11 | MAA13AA210 | YB11 | TURBINE CASING DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46830 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA13AA210 | YB12 | MAA13AA210 | YB12 | TURBINE CASING DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46830 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | -1 | MAA13AA210 | YB96 | MAA13AA210 | YB96 | TURBINE CASING DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46830 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA14AA210 | YB61 | MAA14AA210 | YB61 | ADMISSION STEAM DRAIN VALVE | - |  | Commands | [9 empty] | VALVE |  |  |  |  | VALVE | 46831 |  | write | WORD | 192.168.100.20 | 192.168.100.120
A | 1 | MAA14AA210 | YB11 | MAA14AA210 | YB11 | ADMISSION STEAM DRAIN VALVE | - |  | Command on | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46831 | 0 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA14AA210 | YB12 | MAA14AA210 | YB12 | ADMISSION STEAM DRAIN VALVE | - |  | Command off | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46831 | 1 | write | BOOL | 192.168.100.20 | 192.168.100.120
A | 1 | MAA14AA210 | YB96 | MAA14AA210 | YB96 | ADMISSION STEAM DRAIN VALVE | - |  | Reset operator request | 1 | bin | 0 | [6 empty] | VALVE |  |  |  |  | VALVE | 46831 | 7 | write | BOOL | 192.168.100.20 | 192.168.100.120

## COVER TYPICALS
MODBUS TYPICALS
COVER PAGE

## TYPICALS
ID | USED IN PROJECT | TYPE 1 | Data Type TCS | TYPE 3-MODBUS | TYP 3-OFFSET | BIT | DESCRIPTION | DESCRIPTION_DETAILS | DIRECTION | SIGNAL IN TCS | EXAMPLE MODBUS REGISTER | REMARKS
1 | x | SINGLE ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 0 |  | Signal | Signal | read ---> DCS | XQ60 | 40017 | SINGLE ANALOG MEASUREMENT
2 | x | SINGLE ANALOG MEASUREMENT | SINGLE FLOAT | WORD | 2 |  | Status | Status | read ---> DCS | XQ61 | 40019
3 | x | SINGLE ANALOG MEASUREMENT | BOOLEAN | BOOL | 2 | 0 | Fault | Fault | read ---> DCS | XM20
4 | x | SINGLE ANALOG MEASUREMENT | BOOLEAN | BOOL | 2 | 1 | Alarm low | Alarm low | read ---> DCS | XH54
5 | x | SINGLE ANALOG MEASUREMENT | BOOLEAN | BOOL | 2 | 2 | Warning low | Warning low | read ---> DCS | XH52
6 | x | SINGLE ANALOG MEASUREMENT | BOOLEAN | BOOL | 2 | 3 | Warning high | Warning high | read ---> DCS | XH01
7 | x | SINGLE ANALOG MEASUREMENT | BOOLEAN | BOOL | 2 | 4 | Alarm high | Alarm high | read ---> DCS | XH03
8 | x | ANALOG SEND | SINGLE FLOAT | REAL | 0 |  | Signal | Signal | read ---> DCS | X... Variable | 40017 | SINGLE ANALOG VALUE WITHOUT STATUS
9 | x | 2oo3 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 0 |  | 2oo3 value | 2oo3 value | read ---> DCS | XQ60 | 41005 | 2oo3 ANALOG MEASUREMENT
10 | x | 2oo3 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 2 |  | Single value 1 | Single value 1 | read ---> DCS | XQ71 | 41007
11 | x | 2oo3 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 4 |  | Single value 2 | Single value 2 | read ---> DCS | XQ72 | 41009
12 | x | 2oo3 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 6 |  | Single value 3 | Single value 3 | read ---> DCS | XQ73 | 41011
13 | x | 2oo3 ANALOG MEASUREMENT | SINGLE FLOAT | WORD | 8 |  | Status | Status | read ---> DCS | XQ61 | 41013
14 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 0 | Fault 2oo3 | Fault 2oo3 | read ---> DCS | XM38
15 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 1 | Alarm low | Alarm low | read ---> DCS | XH54
16 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 2 | Warning low | Warning low | read ---> DCS | XH52
17 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 3 | Warning high | Warning high | read ---> DCS | XH01
18 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 4 | Alarm high | Alarm high | read ---> DCS | XH03
19 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 5 | Fault value 1 | Fault value 1 | read ---> DCS | XM31
20 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 6 | Fault value 2 | Fault value 2 | read ---> DCS | XM32
21 | x | 2oo3 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 7 | Fault value 3 | Fault value 3 | read ---> DCS | XM33
22 | x | ANALOG RECEIVE | SINGLE FLOAT | REAL | 0 |  | Signal receive | Signal receive | write <--- DCS | X... Variable | 44681 | RECEIVE VALUE FROM DCS
23 | x | SINGLE BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 0..15 | Signal | Signal | read ---> DCS | X... Variable | 43076 (Bit 13) | SINGLE BINARY MEASUREMENT
24 | x | 2oo3 BINARY MEASUREMENT | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XQ61 | 40198 | 2oo3 BINARY MEASUREMENTS
25 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 0 | 2oo3 signal | 2oo3 signal | read ---> DCS | X... Variable
26 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 1 | Single signal 1 | Single signal 1 | read ---> DCS | XB11
27 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 2 | Single signal 2 | Single signal 2 | read ---> DCS | XB12
28 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 3 | Single signal 3 | Single signal 3 | read ---> DCS | XB13
29 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 4 | Fault | Fault | read ---> DCS | XM38
30 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 5 | Fault signal 1 | Fault signal 1 | read ---> DCS | XM01
31 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 6 | Fault signal 2 | Fault signal 2 | read ---> DCS | XM02
32 | x | 2oo3 BINARY MEASUREMENT | BOOLEAN | BOOL | 0 | 7 | Fault signal 3 | Fault signal 3 | read ---> DCS | XM03
33 | x | SINGLE BINARY RECEIVE | BOOLEAN | BOOL | 0 | 0..15 | Binary receive | Binary receive | write <--- DCS | X... Variable | 44683 (Bit 14) | RECEIVE BINARY FROM DCS
34 | x | SINGLE COMMAND RECEIVE | BOOLEAN | BOOL | 0 | 0..15 | Commands receive | Commands receive | write <--- DCS | X... Variable | 44684 (Bit 15) | RECEIVE COMMANDS FROM DCS
35 | x | CONTROLLER 1 | SINGLE FLOAT | REAL | 0 |  | Actual set point closed loop | Actual set point closed loop | read ---> DCS | XQ51 | 44185 | CONTROLLER GENERAL
36 | x | CONTROLLER 1 | SINGLE FLOAT | REAL | 2 |  | Actual set point open loop | Actual set point open loop | read ---> DCS | XQ52 | 44187
37 | x | CONTROLLER 1 | WORD | WORD | 4 |  | Status | Status | read ---> DCS | XC61 | 44189
38 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 0 | Feedback closed loop | Feedback closed loop | read ---> DCS | XC01
39 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 1 | Feedback open loop | Feedback open loop | read ---> DCS | XC02
40 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 4 | Fault | Fault | read ---> DCS | XC20
41 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 5 | Ready for DCS set point link-on clc | Ready for DCS set point link-on clc | read ---> DCS | XC81
42 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 6 | Ready for DCS set point link-on olc | Ready for DCS set point link-on olc | read ---> DCS | XC82
43 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 7 | Tracking command clc set point | Tracking command clc set point | read ---> DCS | XC91
44 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 8 | Tracking command olc set point | Tracking command olc set point | read ---> DCS | XC92
45 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 9 | Protection on | Protection on | read ---> DCS | ZB01
46 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 10 | Protection off | Protection off | read ---> DCS | ZB02
47 | x | CONTROLLER 1 | BOOLEAN | BOOL | 4 | 11 | Operator request | Operator request | read ---> DCS | XC98
48 | x | CONTROLLER 1 | SINGLE FLOAT | REAL | 5000 |  | DCS set point signal clc | DCS set point signal clc | write <--- DCS | YQ51 | 44685
49 | x | CONTROLLER 1 | SINGLE FLOAT | REAL | 5002 |  | DCS set point signal olc | DCS set point signal olc | write <--- DCS | YQ52 | 44687
50 | x | CONTROLLER 1 | BOOLEAN | BOOL | 5004 | 0 | Command closed loop | Command closed loop | write <--- DCS | YC01
51 | x | CONTROLLER 1 | BOOLEAN | BOOL | 5004 | 1 | Command open loop | Command open loop | write <--- DCS | YC02
52 | x | CONTROLLER 1 | BOOLEAN | BOOL | 5004 | 2 | Command DCS setpoint link-on | Command DCS setpoint link-on | write <--- DCS | YC10
53 | x | CONTROLLER 1 | BOOLEAN | BOOL | 5004 | 11 | Reset operator request | Reset operator request | write <--- DCS | YC98
54 | x | CONTROLLER 2 | BOOLEAN | BOOL | 0 | 0..15 | Status | Status | read ---> DCS | X... Variable | 44189 (Bit 9) | CONTROLLER ACTIVE
55 | x | ON / OFF SELECTION | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XA61 | 44116 | ON / OFF SELECTION
56 | x | ON / OFF SELECTION | BOOLEAN | BOOL | 0 | 0 | Feedback on | Feedback on | read ---> DCS | XA01
57 | x | ON / OFF SELECTION | BOOLEAN | BOOL | 0 | 1 | Feedback off | Feedback off | read ---> DCS | XA02
58 | x | ON / OFF SELECTION | BOOLEAN | BOOL | 0 | 2 | Release on | Release on | read ---> DCS | XA03
59 | x | ON / OFF SELECTION | BOOLEAN | BOOL | 0 | 3 | Release off | Release off | read ---> DCS | XA04
60 | x | ON / OFF SELECTION | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YA61 | 44628 | ON / OFF SELECTION
61 | x | ON / OFF SELECTION | BOOLEAN | BOOL | 5000 | 0 | Command on | Command on | write <--- DCS | YA11
62 | x | ON / OFF SELECTION | BOOLEAN | BOOL | 5000 | 1 | Command off | Command off | write <--- DCS | YA12
63 | x | PRE-SELECTION | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XA61 | 44125 | PRE SELECTION OF DEVICES
64 | x | PRE-SELECTION | BOOLEAN | BOOL | 0 | 0 | Device 1 selected | Device 1 selected | read ---> DCS | XA11
65 | x | PRE-SELECTION | BOOLEAN | BOOL | 0 | 1 | Device 2 selected | Device 2 selected | read ---> DCS | XA12
67 | x | PRE-SELECTION | BOOLEAN | BOOL | 0 | 3 | Release on | Release on | read ---> DCS | XA03
68 | x | PRE-SELECTION | BOOLEAN | BOOL | 0 | 4 | Release off | Release off | read ---> DCS | XA04
69 | x | PRE-SELECTION | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YA61 | 44651 | PRE SELECTION OF DEVICES
70 | x | PRE-SELECTION | BOOLEAN | BOOL | 5000 | 0 | Command device 1 select | Command device 1 select | write <--- DCS | YA21
71 | x | PRE-SELECTION | BOOLEAN | BOOL | 5000 | 1 | Command device 2 select | Command device 2 select | write <--- DCS | YA22
73 | x | DEVICE CHANGEOVER | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XA61 | 44119 | DEVICE CHANGEOVER
74 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 0 | Feedback on | Feedback on | read ---> DCS | XA01
75 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 1 | Feedback off | Feedback off | read ---> DCS | XA02
76 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 2 | Release on | Release on | read ---> DCS | XA03
77 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 3 | Release off | Release off | read ---> DCS | XA04
78 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 4 | Device 1 selected | Device 1 selected | read ---> DCS | XA11
79 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 5 | Device 2 selected | Device 2 selected | read ---> DCS | XA12
81 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 7 | Fault | Fault | read ---> DCS | XA20
82 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 0 | 8 | Operator request | Operator request | read ---> DCS | XA96
83 | x | DEVICE CHANGEOVER | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YA61 | 44631 | DEVICE CHANGEOVER
84 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 5000 | 0 | Command on | Command on | write <--- DCS | YA11
85 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 5000 | 1 | Command off | Command off | write <--- DCS | YA12
86 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 5000 | 4 | Command device 1 select | Command device 1 select | write <--- DCS | YA21
87 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 5000 | 5 | Command device 2 select | Command device 2 select | write <--- DCS | YA22
89 | x | DEVICE CHANGEOVER | BOOLEAN | BOOL | 5000 | 8 | Reset operator request | Reset operator request | write <--- DCS | YA96
90 | x | MOTOR | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XB61 | 44104 | MOTOR
91 | x | MOTOR | BOOLEAN | BOOL | 0 | 0 | Feedback on | Feedback on | read ---> DCS | XB01
92 | x | MOTOR | BOOLEAN | BOOL | 0 | 1 | Feedback off | Feedback off | read ---> DCS | XB02
93 | x | MOTOR | BOOLEAN | BOOL | 0 | 2 | Release on | Release on | read ---> DCS | XB03
94 | x | MOTOR | BOOLEAN | BOOL | 0 | 3 | Release off | Release off | read ---> DCS | XB04
95 | x | MOTOR | BOOLEAN | BOOL | 0 | 6 | Fault | Fault | read ---> DCS | XB20
96 | x | MOTOR | BOOLEAN | BOOL | 0 | 7 | Operator request | Operator request | read ---> DCS | XB96
97 | x | MOTOR | BOOLEAN | BOOL | 0 | 8 | Protection on | Protection on | read ---> DCS | ZB01
98 | x | MOTOR | BOOLEAN | BOOL | 0 | 9 | Protection off | Protection off | read ---> DCS | ZB02
99 | x | MOTOR | BOOLEAN | BOOL | 0 | 10 | Feedback auto | Feedback auto | read ---> DCS | XA01
100 | x | MOTOR | BOOLEAN | BOOL | 0 | 11 | Feedback manual | Feedback manual | read ---> DCS | XA02
101 | x | MOTOR | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YB61 | 44616 | MOTOR
102 | x | MOTOR | BOOLEAN | BOOL | 5000 | 0 | Command on | Command on | write <--- DCS | YB11
103 | x | MOTOR | BOOLEAN | BOOL | 5000 | 1 | Command off | Command off | write <--- DCS | YB12
104 | x | MOTOR | BOOLEAN | BOOL | 5000 | 7 | Reset operator request | Reset operator request | write <--- DCS | YB96
105 | x | MOTOR | BOOLEAN | BOOL | 5000 | 10 | Command auto | Command auto | write <--- DCS | YA01
106 | x | MOTOR | BOOLEAN | BOOL | 5000 | 11 | Command manual | Command manual | write <--- DCS | YA02
107 | x | VALVE | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XB61 | 44219 | SOLENOID VALVES
108 | x | VALVE | BOOLEAN | BOOL | 0 | 0 | Feedback on | Feedback on | read ---> DCS | XB01
109 | x | VALVE | BOOLEAN | BOOL | 0 | 1 | Feedback off | Feedback off | read ---> DCS | XB02
110 | x | VALVE | BOOLEAN | BOOL | 0 | 2 | Release on | Release on | read ---> DCS | XB03
111 | x | VALVE | BOOLEAN | BOOL | 0 | 3 | Release off | Release off | read ---> DCS | XB04
112 | x | VALVE | BOOLEAN | BOOL | 0 | 4 | Fault | Fault | read ---> DCS | XB20
113 | x | VALVE | BOOLEAN | BOOL | 0 | 7 | Operator request | Operator request | read ---> DCS | XB96
114 | x | VALVE | BOOLEAN | BOOL | 0 | 8 | Protection on | Protection on | read ---> DCS | ZB01
115 | x | VALVE | BOOLEAN | BOOL | 0 | 9 | Protection off | Protection off | read ---> DCS | ZB02
118 | x | VALVE | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YB61 | 44731 | SOLENOID VALVES
119 | x | VALVE | BOOLEAN | BOOL | 5000 | 0 | Command on | Command on | write <--- DCS | YB11
120 | x | VALVE | BOOLEAN | BOOL | 5000 | 1 | Command off | Command off | write <--- DCS | YB12
121 | x | VALVE | BOOLEAN | BOOL | 5000 | 7 | Reset operator request | Reset operator request | write <--- DCS | YB96
124 | x | VALVE ACTUATOR | SINGLE FLOAT | REAL | 0 |  | Valve position | Valve position | read ---> DCS | XQ01 | 44220 | VALVE WITH ACTUATOR
125 | x | VALVE ACTUATOR | WORD | WORD | 2 |  | Status | Status | read ---> DCS | XB61 | 44222
126 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 2 | 0 | Feedback open | Feedback open | read ---> DCS | XB01
127 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 2 | 1 | Feedback closed | Feedback closed | read ---> DCS | XB02
128 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 2 | 2 | Release on | Release on | read ---> DCS | XB03
129 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 2 | 3 | Release off | Release off | read ---> DCS | XB04
130 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 2 | 4 | Fault | Fault | read ---> DCS | XB20
131 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 2 | 5 | Operator request | Operator request | read ---> DCS | XB96
132 | x | VALVE ACTUATOR | SINGLE FLOAT | REAL | 5000 |  | Spare | Spare | write <--- DCS | XQ01 | 44220 | VALVE WITH ACTUATOR
133 | x | VALVE ACTUATOR | WORD | WORD | 5002 |  | Commands | Commands | write <--- DCS | YB61 | 447222
134 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 5002 | 0 | Command open | Command open | write <--- DCS | YB11
135 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 5002 | 1 | Command close | Command close | write <--- DCS | YB12
136 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 5002 | 2 | Command stop | Command stop | write <--- DCS | YB13
137 | x | VALVE ACTUATOR | BOOLEAN | BOOL | 5002 | 5 | Reset operator request | Reset operator request | write <--- DCS | YB96
138 | x | VALVE ACTUATOR DCS | SINGLE FLOAT | REAL | 0 |  | Valve position setpoint | Valve position setpoint | read ---> DCS | YQ01 | 44740 | VALVE WITH POSITION FROM DCS
139 | x | VALVE ACTUATOR DCS | WORD | WORD | 2 |  | Commands send | Commands send | read ---> DCS | YB61 | 44136
143 | x | VALVE ACTUATOR DCS | SINGLE FLOAT | REAL | 5000 |  | Valve position receive | Valve position receive | write <--- DCS | XQ01 | 44740 | VALVE WITH POSITION FROM DCS
144 | x | VALVE ACTUATOR DCS | WORD | WORD | 5002 |  | Status receive | Status receive | write <--- DCS | XB61 | 44742
145 | x | VALVE ACTUATOR DCS | BOOLEAN | BOOL | 5002 | 0 | Feedback open | Feedback open | write <--- DCS | XB01
146 | x | VALVE ACTUATOR DCS | BOOLEAN | BOOL | 5002 | 1 | Feedback closed | Feedback closed | write <--- DCS | XB02
147 | x | VALVE ACTUATOR DCS | BOOLEAN | BOOL | 5002 | 4 | Fault | Fault | write <--- DCS | XB20
148 | x | VALVE DCS | WORD | WORD | 0 |  | Commands | Commands | read ---> DCS | YB61 | 44219 | SOLENOID VALVES FROM DCS
149 | x | VALVE DCS | BOOLEAN | BOOL | 0 | 0 | Command on | Command on | read ---> DCS | YB11
150 | x | VALVE DCS | BOOLEAN | BOOL | 0 | 1 | Command off | Command off | read ---> DCS | YB12
152 | x | VALVE DCS | BOOLEAN | WORD | 5000 |  | Status | Status | write <--- DCS | XB61 | 44731 | SOLENOID VALVES FROM DCS
153 | x | VALVE DCS | BOOLEAN | BOOL | 5000 | 0 | Feedback on | Feedback on | write <--- DCS | XB01
154 | x | VALVE DCS | BOOLEAN | BOOL | 5000 | 1 | Feedback off | Feedback off | write <--- DCS | XB02
155 | x | VALVE DCS | BOOLEAN | BOOL | 5000 | 4 | Fault | Fault | write <--- DCS | XB20
157 | x | STEP SEQUENCE | SINGLE FLOAT | REAL | 0 |  | Step number | Step number | read ---> DCS | XA91 | 44125 | STEP SEQUENCE
158 | x | STEP SEQUENCE | WORD | WORD | 2 |  | Status | Status | read ---> DCS | XA61 | 44127
159 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 0 | Feedback on | Feedback on | read ---> DCS | XA01
160 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 1 | Feedback off | Feedback off | read ---> DCS | XA02
161 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 2 | Release op | Release op | read ---> DCS | XA03
162 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 3 | Release sd | Release sd | read ---> DCS | XA04
163 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 4 | Fault | Fault | read ---> DCS | XA20
164 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 5 | Operation running | Operation running | read ---> DCS | XA08
165 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 6 | Shutdown running | Shutdown running | read ---> DCS | XA09
166 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 8 | Protection operation | Protection operation | read ---> DCS | ZA01
167 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 9 | Protection shutdown | Protection shutdown | read ---> DCS | ZA02
168 | x | STEP SEQUENCE | BOOLEAN | BOOL | 2 | 10 | Operator request | Operator request | read ---> DCS | XA96
169 | x | STEP SEQUENCE | SINGLE FLOAT | REAL | 5000 |  | Spare | Spare | write <--- DCS | YA91 | 49125 | STEP SEQUENCE
170 | x | STEP SEQUENCE | WORD | WORD | 5002 |  | Commands | Commands | write <--- DCS | YA61 | 49127
171 | x | STEP SEQUENCE | BOOLEAN | BOOL | 5002 | 0 | Command on | Command on | write <--- DCS | YA11
172 | x | STEP SEQUENCE | BOOLEAN | BOOL | 5002 | 1 | Command off | Command off | write <--- DCS | YA12
173 | x | STEP SEQUENCE | BOOLEAN | BOOL | 5002 | 2 | Command operation | Command operation | write <--- DCS | YA18
174 | x | STEP SEQUENCE | BOOLEAN | BOOL | 5002 | 3 | Command shutdown | Command shutdown | write <--- DCS | YA19
175 | x | STEP SEQUENCE | BOOLEAN | BOOL | 5002 | 10 | Reset operator request | Reset operator request | write <--- DCS | YA96
176 | x | 1oo2 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 0 |  | 1oo2 value | 1oo2 value | read ---> DCS | XQ60 | 41011 | 2oo3 ANALOG MEASUREMENT
177 | x | 1oo2 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 2 |  | Single value 1 | Single value 1 | read ---> DCS | XQ11 | 41005
178 | x | 1oo2 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 4 |  | Single value 2 | Single value 2 | read ---> DCS | XQ12 | 41007
179 | x | 1oo2 ANALOG MEASUREMENT | SINGLE FLOAT | REAL | 6 |  | Spare | Spare | read ---> DCS | XQ13 | 41009
180 | x | 1oo2 ANALOG MEASUREMENT | SINGLE FLOAT | WORD | 8 |  | Status | Status | read ---> DCS | XQ61 | 41013
181 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 0 | Fault 1oo2 | Fault 1oo2 | read ---> DCS | XM38
182 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 1 | Alarm low | Alarm low | read ---> DCS | XH54
183 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 2 | Warning low | Warning low | read ---> DCS | XH52
184 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 3 | Warning high | Warning high | read ---> DCS | XH01
185 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 4 | Alarm high | Alarm high | read ---> DCS | XH03
186 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 5 | Fault value 1 | Fault value 1 | read ---> DCS | XM31
187 | x | 1oo2 ANALOG MEASUREMENT | BOOLEAN | BOOL | 8 | 6 | Fault value 2 | Fault value 2 | read ---> DCS | XM32
188 | x | SETPOINT | SINGLE FLOAT | REAL | 0 |  | Actual set point | Actual set point | read ---> DCS | XQ52 | 44125 | SETPOINT ADJUSTER
189 | x | SETPOINT | WORD | WORD | 2 |  | Status | Status | read ---> DCS | XC61 | 44127
190 | x | SETPOINT | BOOLEAN | BOOL | 2 | 0 | Fault | Fault | read ---> DCS | XC20
191 | x | SETPOINT | BOOLEAN | BOOL | 2 | 1 | Ready for DCS set point | Ready for DCS set point | read ---> DCS | XC82
192 | x | SETPOINT | SINGLE FLOAT | REAL | 5000 |  | DCS set point | DCS set point | write <--- DCS | YQ52 | 49125 | SETPOINT ADJUSTER
193 | x | SETPOINT | WORD | WORD | 5002 |  | Commands | Commands | write <--- DCS | YC61 | 49127
194 | x | SETPOINT | SINGLE FLOAT | REAL | 5000 |  | DCS set point | DCS set point | write <--- DCS | YQ52 | 49125 | SETPOINT ADJUSTER
195 | x | SETPOINT | WORD | WORD | 5002 |  | Commands | Commands | write <--- DCS | YC61 | 49127
196 | x | SETPOINT | BOOLEAN | BOOL | 5002 | 0 | Command DCS setpoint link-on | Command DCS setpoint link-on | write <--- DCS | YC10
197 | x | MOTOR with DCO | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XB61 | 44104 | MOTOR
198 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 0 | Feedback on | Feedback on | read ---> DCS | XB01
199 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 1 | Feedback off | Feedback off | read ---> DCS | XB02
200 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 2 | Release on | Release on | read ---> DCS | XB03
201 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 3 | Release off | Release off | read ---> DCS | XB04
202 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 6 | Fault | Fault | read ---> DCS | XB20
203 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 7 | Operator request | Operator request | read ---> DCS | XB96
204 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 8 | Protection on | Protection on | read ---> DCS | ZB01
205 | x | MOTOR with DCO | BOOLEAN | BOOL | 0 | 9 | Protection off | Protection off | read ---> DCS | ZB02
208 | x | MOTOR with DCO | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YB61 | 44616 | MOTOR
209 | x | MOTOR with DCO | BOOLEAN | BOOL | 5000 | 0 | Command on | Command on | write <--- DCS | YB11
210 | x | MOTOR with DCO | BOOLEAN | BOOL | 5000 | 1 | Command off | Command off | write <--- DCS | YB12
211 | x | MOTOR with DCO | BOOLEAN | BOOL | 5000 | 7 | Reset operator request | Reset operator request | write <--- DCS | YB96
214 | x | VALVE with DCO | WORD | WORD | 0 |  | Status | Status | read ---> DCS | XB61 | 44104 | MOTOR
215 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 0 | Feedback on | Feedback on | read ---> DCS | XB01
216 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 1 | Feedback off | Feedback off | read ---> DCS | XB02
217 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 2 | Release on | Release on | read ---> DCS | XB03
218 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 3 | Release off | Release off | read ---> DCS | XB04
219 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 6 | Fault | Fault | read ---> DCS | XB20
220 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 7 | Operator request | Operator request | read ---> DCS | XB96
221 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 8 | Protection on | Protection on | read ---> DCS | ZB01
222 | x | VALVE with DCO | BOOLEAN | BOOL | 0 | 9 | Protection off | Protection off | read ---> DCS | ZB02
225 | x | VALVE with DCO | WORD | WORD | 5000 |  | Commands | Commands | write <--- DCS | YB61 | 44616 | MOTOR
226 | x | VALVE with DCO | BOOLEAN | BOOL | 5000 | 0 | Command on | Command on | write <--- DCS | YB11
227 | x | VALVE with DCO | BOOLEAN | BOOL | 5000 | 1 | Command off | Command off | write <--- DCS | YB12
228 | x | VALVE with DCO | BOOLEAN | BOOL | 5000 | 7 | Reset operator request | Reset operator request | write <--- DCS | YB96